## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | Dirning | 6150 | 6243 | 4400 | 4399 | 1750 | 1844 | 28.46% | 29.54%
RTU-2 | Kitchen | 6150 | 6355 | 4450 | 4570 | 1700 | 1785 | 27.64% | 28.09%
PRV-1 | Restroom | [12 empty] | 375 | 369
PRV-2 | HD1 Griddle | [10 empty] | 1500 | 1592
PRV-3 | HD2 Fryer | [10 empty] | 1500 | 1554
EF-1A | Mop Room | [12 empty] | 75 | 70
TOTALS |  | 12300 | 12598 | 8850 | 8969 | 3450 | 3629 |  |  | 0 | 0 | 3000 | 3146 | 450 | 439
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3450 | 3629 |  | FRONT |  | 0.009 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3450 | 3585 |  | SIDE |  | 0.009 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 0 | 44 |  | REAR |  | 0.009 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.009 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0