## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 1929 | 1929 | 1929 | 1929 | 0 | 0 | 0% | 0%
RTU-2 | BAR | 2192 | 2192 |  | 2192 | 0 | 0 | 0% | 0%
RTU-3 | DINING LEFT | 2460 | 2460 | 1983 | 1983 | 477 | 477 | 19.39% | 19.39%
RTU-4 | DINING | 4456 | 4456 | 3538 | 3358 | 918 | 918 | 20.6% | 20.6%
MUA-1 | KITCHEN HD | [9 empty] | 550
EF-1 | KITCHEN HD | [10 empty] | 1808 | 1808
EF-2 | KITCHEN HD | [10 empty] | 2902 | 2902
EF-3 | KITCHEN HD | [11 empty] | 0
EF-4 | KITCHEN HD | [10 empty] | 184 | 184
EF-5
EF-6
EF-7 | RESTROOM | [12 empty] | 400 | 400
TOTALS |  | 11037 | 11037 | 7450 | 9462 | 1395 | 1395 |  |  | 0 | 550 | 4894 | 4894 | 400 | 400
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | TRUE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 1395 | 1945 |  | FRONT |  | -0.0221 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 5294 | 5294 |  | SIDE |  | -0.0223 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | -3899 | -3349 |  | REAR | [10 empty] | FALSE
[5 empty] | AVERAGE |  | -0.0222 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES:
Unable to get a good pressure reading from back door.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0