## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN/ BOH | 9500 | 9367 | 8450 | 8296 | 1050 | 1071 | 11.05% | 11.43%
AC-2 | DRIVE THRU | 5600 | 5524 | 4025 | 3987 | 1575 | 1537 | 28.12% | 27.82%
AC-3 | DINNING /RR | 6400 | 6705 | 4375 | 4724 | 2025 | 1981 | 31.64% | 29.55%
AC-4 | BOH |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
AC-5 | PLAY AREA |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
AC-6 | BOH |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
EF-1 | HD 1 | [10 empty] | 1913 | 1907
EF-2 | HD 2 & 3 | [10 empty] | 1402 | 1426
EF-3 | RESTROOMS | [12 empty] | 300 | 306
EF4 | RESTROOMS
TOTALS |  | 21500 | 21596 | 16850 | 17007 | 4650 | 4589 |  |  | 0 | 0 | 3315 | 3333 | 300 | 306
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4650 | 4589 |  | FRONT |  | 0.0152 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3615 | 3639 |  | SIDE |  | 0.0156 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 1035 | 950 |  | REAR |  | 0.0139 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0149 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390