# Asset Walk 6-9 weeks

Project: Triarc Tank

| Date of Walk-Thru | 07/05/2023 |
| --- | --- |
| AHU/RTU |  |
| RA & OA damper installed | Yes |
| Piping complete | Yes |
| Ductwork Connections Finalized and Sealed to Unit (OA, Return, Relief, Supply) | Yes |
| Power Landed to Unit/VFD | Yes |
| Comments |  |
| Exhaust Fans |  |
| Unit Mounted to Correct Curb/Location | Yes |
| Disconnect Available | Yes |
| Power to Fans/VFD | Yes |
| Duct connected to fan/curb | Yes |
| Motorized Dampers Installed | Yes |
| Comments |  |
| Return Air Path (marked up drawing attached) |  |
| Are there enough transfer openings | Yes |
| Are they sized correctly | Yes |
| Are they in the correct location | ## Yes ## Notes/Comments: ## Notes/Comments: |
| Comments | ## Transfer missing Rm 405 , 2 transfers added in Rm 409. |
| VAVs |  |
| VAV Hanging & Present | ## Yes |
| Inlet Duct connected | ## Yes |
| Discharge Duct connected | ## Yes |
| Unit Powered & Operational | ## Yes |
| Piping to reheat coil complete | ## Yes |
| Balance dampers installed and open | ## Yes |
| Comments |  |

2 new Transfers Here:  							Missing Transfer Here:

Room 409:

Room 405: