## Sheet1
APPENDIX *RTU (ROOFTOP UNIT) *EH (ENTRY HEATER) *ERV (ENERGY RECOVERY VENTILATOR) *EF (EXHAUST FAN) *CU (SPLIT SYSTEM- COMPRESOR UNIT) *AHU(SPLIT SYSTEM-AIR HANDLER) |  |  | 39 WALGREENS FY24 HVAC SITE SURVEY CHECKLIST
Date: | 2023-02-02 | Store#: | 39 | Address: | 235 E Palatine Rd
| EQUIPMENT DATA | [7 empty] | COOLING | HEATING |  | SMOKE DETECTOR |  | POWER SUPPLY |  |  |  | CURB MEASUREMENTS
RTU DATA | Area Served (LOCATION) EX: Front Sales Pharmacy Storage PARTNER SPACE etc | DATE OF MFG. | EF (ROOF MOUNTED/IN-LINE) | MAKE | MODEL # | SERIAL # | INTERNAL & EXTERNAL UNIT CONDITION COMMENTS & NOTES: (*Give Full Details On Each Unit*) |  | CAPACITY TONS | HEAT TYPE PROPANE / NATURAL GAS / ELECTRIC / HEAT PUMP - AUX HEAT KW | HEATING CAPACITY MAX INPUT(BTU / KW) | LOCATION (UNIT / DUCT) | DUCT LOCATION (SUPPLY / RETURN) | GFI POWERED (Y/N) (BLDG. / RTU) | VOLTAGE (NAMEPLATE) | VOLTAGE (MEASURED) | PHASE | EXISTING CURB ADAPTER (YES/NO) | CURB MEASUREMENTS O.D. | UNIT MEASUREMENTS O.D.
RTU 1 | Front Sales | 2012 | FY24 Inventory Reduction | Trane | YCD181F4CLAA | 121610003D | York / AES FY24 AL Inventory AV15N3DP4S1CDS42B2 / N2M3001822, Reheat, No DCV, Economizer, Curb Adapter Required. Fair condition, no issues observed |  | 15 | Gas | 350000 | Duct | Return | RTU | 460 | 460 | 3 | Yes | 90x70 | 122x85
RTU 2 | Back Sales | 2012 | FY24 Inventory Reduction | Trane | YCD181F4CLAA | 121610021D | York / AES FY24 AL Inventory ZT150N18R4B5GCB2R2 / N2K3860014, DCV, Economizer, Curb Adapter Required. Fair condition, no issues observed |  | 15 | Gas | 350000 | Duct | Return | RTU | 460 | 460 | 3 | Yes | 90x70 | 122x85
RTU 3 | Cosmetic Sales | 2012 | FY24 Inventory Reduction | Trane | YHC060ERHA16D0A0A | 121710037L | York / AES FY24 WV Inventory ZJ049N12D4B5GCA2R3 / N2K3859613, DCV, Economizer, Curb Adapter Required. Fair condition, no issues observed |  | 5 | Gas | 130000 | Duct | Return | BLDG | 460 | 460 | 3 | Yes | 71x41 | 87x53
RTU 4 | Abandoned - Vacant lease Space | 1981 | Remove from Roof & Cap Curb | Trane | SFCB-B753-HA | C81F-09385 | Abandoned Vacant Lease Space. Remove and Cap Curb. Poor condition, rust and wear present |  | 4.5 | GAS | 250000 | DUCT | RETURN | BLDG | 208 | 208 | 3 | YES | 66x44 | 75x53
RTU 5 | Pharmacy | 2012 | FY24 Inventory Reduction | Trane | YHC060E4RMA16D0A0A | 121511888L | York / Arris FY24 AL Inventory (AES TO P/U AT Arris) ZJ061N16D4B5GCA2R4 / N2M3992001, DCV, Economizer, Curb Adapter Required. Fair condition, no issues observed |  | 5 | Gas | 80000 | Duct | Return | BLDG | 460 | 460 | 3 | Yes | 75x37 | 87x53
RTU 6
RTU 7
EH | Entrance | 1981 | FY24 Inventory Reduction | Dravo Hastings | DMUAE210V | 37926 | York / Sterling New Production PV-15 Entry Heater, 150,000 Gas Input, 115/1/60 Voltage, Custom Curb Adapter - See Pictures of Unit. Fair condition, no issues observed |  | N/A | Gas | 200000 | Unit | Return | N/A | 115 | 115 | 1 | No | 107x36 | 134x39.5
SPLIT SYSTEM DATA
CU 1 | [6 empty] | *include line set sizes*
CU 2 | [6 empty] | *include line set sizes*
CU 3 | [6 empty] | *include line set sizes*
AHU 1
AHU 2
AHU 3
VENTILATION DATA
ERV 1
ERV 2
EF 1 | Restrooms | N/L | Inline | Greenheck | No Tag | No Tag | Replace Ceiling Exhaust Fan(s) - Poor condition, restroom smell does not exhaust, tag is blank |  | N/A | N/A | N/A | N/A | N/A | N/A | No Tag | No Safe Access | No Tag | N/A | N/A | N/A
EF 2 | Electrical Room | N/L | Inline | Broan | No Tag | No Tag | Replace Ceiling Exhaust Fan- Poor condition, not operating, no tag |  | N/A | N/A | N/A | N/A | N/A | N/A | No Tag | No Safe Access | No Tag | N/A | N/A | N/A
EF 3
EF 4
EF 5
EF 6
EF 7
REFRIGERATION DATA
Roof mounted condenser
Roof mounted condenser
Roof mounted condenser
Roof mounted condenser
General Store Notes | [6 empty] | Electrical Panel Information | FUSED SWITCH OR BREAKER | FUSE / BREAKER BRAND | FUSE / BREAKER MODEL # | RATING(AMPS) | WIRE SIZE | CONDUIT SIZE AT UNIT
Former Rite Aid (Y/N): | N | [5 empty] | RTU-1 | Breaker | Siemens | N/L | 60 | 10 AWG | 1.5"
Partner Tenant (included but not lmited to: ex. Village Medical (VMD), LabCorp, Novant, and MedExpress) | N |  | Provid partner name |  |  |  | RTU-2 | Breaker | Siemens | N/L | 60 | 10 AWG | 1.5"
If Partner Tenant Exists do they have full height walls? (Y/N) | N/A |  | Full height walls are defined as walls up to ceiling.
Obvious "non-typical" Heat Load (Y/N) provide detail in note section | N |  | Ex.: Floor to glass windows, Sky Lights, Permanent Heat Productin Displays, Etc (please make high level note of any potential items.) |  |  |  | RTU-3 | Breaker | Siemens | N/L | 30 | 14 AWG | 1.5"
Tenant Space (Y/N): | N |  | Tenant Name (VMD/Kroger/LabCorp, etc.): |  |  |  | RTU-4
Photo Lab (Y/N): | Y |  | Dry/Wet Lab: Dry
Roof Condition (Good/Fair/Poor): | Good | [5 empty] | RTU-5 | Breaker | Siemens | N/L | 20 | 14 AWG | 1.5"
Ductwork Type (Galvanized, Duct Board, Sock Duct, Other) | Galvanized |  | If "Other" Specify Type: |  |  |  | RTU-6
Unit Hail Damage (Y/N): | N | [5 empty] | RTU-7
Store within 20 Miles of Ocean? (Y/N): | N
Existing EMS (Y/N): | Y |  | EMS Type(FSG/Gridpoint): Gridpoint EC-2000
Fire Alarm Panel Operational (Y/N): | N/A |  | Panel Model#:
Photo of Fire Alarm Panel Taken (Y/N): | N/A
Main Refrigeration Type (Remote Condensing Unit or Self-Contained) | Self-Contained
Main Refridgeration Type (Walk-In or Reach-In) | Freezer: Reach-In
Cooler: Reach-In
Self-Contained Refrigeration ONLY Door Count: | Freezer: 6
Cooler: 12
Obvious Visual Damage to MDP (Y/N): | N |  | Explain Visual Damage:
Notes for Installer: | Recommendation: Replace (4) 2012 Trane RTUs, (1) 1981 Entry Heater, (3) Ceiling Exhaust Fans. Replace RTUs with FY24 Inventory units. AES to P/U (1) 5 Ton RTU from Arris AL. Replace Entry Heater with new Production Unit as noted on survey Form. IC to install interior humidity sensor for RTU-1 at Existing Zone Temperatuire Sensor location. Connect replacement units to existing GridPoint EC-2000 systems as BACnet Control. Remove and Cap Existing Roof Exhaust Fans that are no longer in use. Remove and cap the Abandoned RTU and Refrigeration Condening unit on the roof. Replace (3) Ceiling Exhaust Fans as noted on Survey Form. Old unit from 1981 is over an unused space behind the pharmacy, used to be RTU-4. All roof mounted fans in photos are unused, only inline exhaust fans at this location. Revisit 04/25/2023: Old unit from 1981 is above a space that is unused by Walgreens and has a "Retail Space Available" sign in the window, the breaker however is in the electrical room inside Walgreens, the breaker is off. The roof mounted fans are also for the unused space. The refrigeration condenser on the roof is turned off at the unit disconnect and is not being used, this store uses self-contained refrigeration units.
Original Curb Dimensional Data
RTU# | RTU1 | RTU2 | RTU3 | RTU4 | RTU5 | RTU6 | RTU7 | EH
Curb Type | Type 3 | Type 3 | Type 3 |  | Type 3 |  |  | Type 3
A (Length) | 122 | 122 | 87 |  | 87 |  |  | 134
B (Width) | 84 | 84 | 53 |  | 53 |  |  | 39.5
E | 28 Supply | 28 Supply | 19.5 Supply |  | 19.5 Supply |  |  | 25 Supply
F | 36 Return | 36 Return | 17 Return |  | 17 Return |  |  | 34 Return
G | 13 | 13 | 9 |  | 9 |  |  | 37
H
I
J
K
L
M
N
O