## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 8125 | 8369 | 6575 | 6805 | 1550 | 1564 | 19.08% | 18.69%
AC-2 | DRIVE THRU | 1750 | 1851 | 1400 | 1496 | 350 | 355 | 20% | 19.18%
AC-3 | DINING/RR | 5250 | 5407 | 4000 | 4095 | 1250 | 1312 | 23.81% | 24.26%
AC-4 | BOH | 1750 | 1812 | 1400 | 1448 | 350 | 364 | 20% | 20.09%
AC-5 | PLAY AREA |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
AC-6 | BOH |  |  | 0
EF-1 | HD 1 | [10 empty] | 1418 | 1345
EF-2 | HD 2 & 3 | [10 empty] | 1091 | 1055
EF-3 | RESTROOMS | [12 empty] | 300 | 300
EF4 | RESTROOMS
EF 5 | HD L1
TOTALS |  | 16875 | 17439 | 13375 | 13844 | 3500 | 3595 |  |  | 0 | 0 | 2509 | 2400 | 300 | 300
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3500 | 3595 |  | FRONT |  | 0.024 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2809 | 2700 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 691 | 895 |  | REAR |  | 0.025 | [8 empty] | FALSE
[5 empty] | AVERAGE |  | 0.0245 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390