## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 8000 | 6819 | 6000 | 5016 | 2000 | 1803 | 25% | 26.44%
AC-2 | DINING A, RR | 1790 | 1779 | 1240 | 1247 | 550 | 532 | 30.73% | 29.9%
AC-3 | DINING B | 2000 | 1980 | 985 | 1390 | 1015 | 590 | 50.75% | 29.8%
AC-4 | DINING B |  | 4307 |  | 3221 | 670 | 1086 | #DIV/0! | 25.21%
AC-5 | PLAY AREA |  | 1751 |  | 1423 | 400 | 328 | #DIV/0! | 18.73%
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1912 | 1886
EF-2 | HOOD 2 | [10 empty] | 1402 | 1345
EF-3 | RESTROOMS | [12 empty] | 300 | 277
TOTALS |  | 11790 | 16636 | 8225 | 12297 | 4635 | 4339 |  |  | 0 | 0 | 3314 | 3231 | 300 | 277
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4635 | 4339 |  | FRONT |  | 0.002 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3614 | 3508 |  | SIDE |  | 0.008 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 1021 | 831 |  | REAR |  | 0.004 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0046667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390