## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 2000 | 2000 |  | 1735 | 235 | 235 | 100% | 100%
RTU-2 | DINING | 4000 | 3625 |  | 2769 | 0 | 856 | 36% | 36%
MUA-1 | KITCHEN HOOD | [9 empty] | 1136
EF-1 | KITCHEN HOOD | [10 empty] | 1898 | 1670
EF-2 | KITCHEN HOOD | [10 empty] | 2020 | 1870
EF-3 | RESTROOM | [12 empty] | 0 | 0
TOTALS |  | 6000 | 5625 | 0 | 4504 | 235 | 1091 |  |  | 0 | 1136 | 3918 | 3540 | 0 | 0
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | TRUE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 235 | 2227 |  | FRONT |  | -0.07 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 3918 | 3540 |  | SIDE |  | -0.09 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | -3683 | -1313 |  | REAR |  | -0.09 | [8 empty] | FALSE
[5 empty] | AVERAGE |  | -0.08 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | CAPTIVE-AIRE |  | SOLO 10 16X16 |  |  |  | ACPSP |  | 183X12 |  | 1950 |  | 3200 |  | -1250