## Sheet1
Summary
What was found initially: | Manager states building is mostly comfortable. The humidity does get high during the summers but due to one of the RTU's being recently replaced the dinning area has stayed coomfortable, building pressure was negative. Units were not set for constant air flow.
Changes made: | EF-1 was abled to be slowed down, EF-2 and EF-3 were able to speed up but will need a pulley change in order to reach target airflow. RTU's parameter 154 as changed to "1" for continous air flow. OA were adjusted on each unit to meet target.
Air balancing & performance related issues that need to be resolved: | The restroom exhuast fan was not able to be sped up due to motor already running over listed amperage. Hood filters were very dirty, EF-2 and EF-3 airflow was low and will need pulley changes in order to speed up the fan to get to target airflow.
Air Balance Schedule
AIR GOING IN (+) | Target | Initial | Final
RTU-1 OA | 1500 | 587 | 1504
RTU-2 OA | 1750 | 1041 | 1690 |  |  |  | Air Going In |  | Air Going out
RTU-3 OA | 1500 | 541 | 1485 |  |  |  | 6033 |  | 4668
RTU-4 OA | 0
RTU-5 OA | 0
RTU-6 OA | 0
MUA-1 | 1237.5 | 1354 | 1354 | 1.0941
MUA-2 | 0
MUA-3 | 0
AIR GOING OUT (-)
EF-1 | 1125 | 1667 | 1217 | 1.4818 | 1.0818
EF-2 | 1350 | 570 | 732 | 0.42222 |  |  |  | Air Going In - Air Going out =
EF-3 | 1575 | 500 | 938 | 0.31746 |  |  |  | 1365
EF-4 | 825 | 747 | 828 | 0.90545
EF-5 Diswasher | 600 | 657 | 657 |  |  |  |  | Building Pressure Average:
EF-6 | 0 | [6 empty] | 0.01
EF-7 | 0
RR Exhaust (Total) | 600 | 296 | 296
NET AIRFLOW (TARGET +200 CFM)
| -87.5 | -914 | 1365
Target Airflow Calculations
Unit | Tonnage | Target OA | OA %
RTU-1 | 15 | 1500 | 25%
RTU-2 | 17.5 | 1750 | 25%
RTU-3 | 15 | 1500 | 25%
RTU-4 |  | 0 | N/A
RTU-5 |  | 0 | N/A
RTU-6 |  | 0 | N/A
Hoods | Served by | Served by | Type | Length (in) | Width (in) | MUA Type | Equipment 1 | Equipment 2 | Equipment 3 | CFM/ft1 | CFM/ft 2 | CFM/ft3 | CFM/ft Target | Target Exhaust | Target MUA
Hood 1 | EF-3 |  | Type I | 84 | 36 |  | Fryers |  |  | 225 | NOT FOUND | NOT FOUND | 225 | 1575 | #N/A
Hood 2 | EF-2 | MUA-1 | Type I | 72 | 57 | Short Cycle | Griddle - Flat Top |  |  | 225 | NOT FOUND | NOT FOUND | 225 | 1350 | 675
Hood 3 | EF-1 | MUA-1 | Type I | 90 | 57 | Short Cycle | Ovens |  |  | 150 | NOT FOUND | NOT FOUND | 150 | 1125 | 562.5
Hood 4 | EF-4 |  | Type I | 66 | 51 |  | Ovens |  |  | 150 | NOT FOUND | NOT FOUND | 150 | 825 | #N/A
Hood 5 | [9 empty] | NOT FOUND | NOT FOUND | NOT FOUND | 0 | 0 | 0
Restrooms | # of Toilets/Urinals | Target CFM
RR Exhaust (Total) | 8 | 600

## Kitchen Equipment
Equipment | CFM/ft
Char Grill | 275
Fryers | 225
Griddle - Flat Top | 225
Ovens | 150
Salamander | 275
Range | 200

## MUA Type
PSP | 0.8
Short Cycle | 0.5
Back Return | 0.5

## Sheet2
EF-1 | MUA-1 | Type I
EF-2 | MUA-2
EF-3 | MUA-3
EF-4
EF-5
EF-6
EF-7