## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 |  | 2175 | 2089 | 1225 | 1142 | 950 | 947 | 43.68% | 45.33%
RTU-2 |  | 5230 | 5093 | 2930 | 2782 | 2300 | 2311 | 43.98% | 45.38%
KEF-1 | [11 empty] | 700 | 690
KEF-2 | [11 empty] | 700 | 700
KEF-3 | [11 empty] | 700 | 690
KEF-4 | [11 empty] | 700 | 719
EF-1 | [13 empty] | 300 | 312
EF-2 | [13 empty] | 200 NOT IN SPACE | 203 NOT IN SPACE
TOTALS |  | 7405 | 7182 | 4155 | 3924 | 3250 | 3258 |  |  | 0 | 0 | 2800 | 2799 | 300 | 312
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3250 | 3258 |  | FRONT |  | 0.0063 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3100 | 3111 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 150 | 147 |  | REAR |  | 0.0052 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.00575 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
KITCHEN PRESSURIZATION (MUST BE NEGATIVE)
TOTALS |  | DESIGN | ACTUAL
TOTAL KITCHEN OA |  | 2300 | 2311
TOTAL KITCHEN EXHAUST |  | 2800 | 2799
NET AIRFLOW |  | -500 | -488
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0