## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 9500 | 8974 | 7500 | 7171 | 2000 | 1803 | 21.05% | 20.09%
AC-2 | DINING A , RR | 2500 | 2353 | 2000 | 1898 | 500 | 455 | 20% | 19.34%
AC-3 | DINING B | 4000 | 3998 | 3200 | 3260 | 800 | 738 | 20% | 18.46%
AC-4 | DINING B | 2765 | 2866 | 2205 | 2293 | 560 | 573 | 20.25% | 19.99%
AC-5 | PLAY AREA | 1800 | 1194 | 1440 | 1061 | 360 | 133 | 20% | 11.14%
AC-6 | BOH | 1200 | 1252 | 960 | 1016 | 240 | 236 | 20% | 18.85%
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1913 | 2002
EF-2 | HD2/HD3 FRYERS | [10 empty] | 701 | 686
EF-3 | RESTROOM | [12 empty] | 400 | 430
EF-3 | RESTROOM | [10 empty] | 701 | 656
TOTALS |  | 21765 | 20637 | 17305 | 16699 | 4460 | 3938 |  |  | 0 | 0 | 3315 | 3344 | 400 | 430
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4460 | 3938 |  | FRONT |  | 0.0213 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3715 | 3774 |  | SIDE |  | 0.021 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 745 | 164 |  | REAR | [10 empty] | FALSE
[5 empty] | AVERAGE |  | 0.02115 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390