Steak 48

Findings Summary

Initial building pressure upon arrival was -0.156’’ After looking through the mechanical plans it was determined that the building was engineered to be negative. Outside airflow designed to enter the building per prints equaled 10,451 cfm. Exhausted airflow per prints added up to equal 13,369 cfm, causing the building to have a design of negative -2918 cfm.

Currently read airflow is OA +8980 cfm. and exhausted air flow at -9930 cfm. This leaving a net airflow of -950 cfm.

-Upon arrival MAU was running at 89% on the ECM. MAU was read at hood psp and also traversed. Hood reading at psp added up to 4311 CFM. MAU traverse was also done reading at 4416 cfm. Upon further inspection MAU intake on the side of the building was covered in dust and dirt and restricting the MAU airflow. Steak 48 is going to have this intake cleaned to allow for proper flow.

-ERV supply airflow was running above design cfm but was not reduced to prevent increasing negative building pressure. Exhaust on ERV was not operational upon arrival; Daikin tech was on site Wednesday Morning and was able to get the exhaust fan to run but was unable to set exhaust fan speed. Exhaust fan was turned back off per the request of Steak 48 to prevent building from becoming further negatively pressured.

-PCU fan total is within design cfm.

-EF1 dish hood is above design cfm currently operating at 1406cfm while design calls for 1125. Per Steak 48 fan has to run at current speed and remain above design to capture dish hood steam. Due to dish hood being undersized.

- building pressure was taken with all equipment turned off,  building pressure was positive neutral +0.003’’ at door

Recommendations

-PCU / each cooking hood be reduced down to lowest speed / cfm possible while still allowing for cooking smoke capture to remain at 100%.

-ERV exhaust to be only run at the necessary speed to allow for restroom exhaust.

-Supply fan on ERV to remain above design cfm. currently operating at 4669 cfm. design 4000. Fan is operating below FLA.

-MAU to be retraversed for new total after intake has been cleaned.

- Dish hood to also be reduced to design cfm.