## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 3000 | 3096 | 2200 | 2291 | 800 | 805 | 26.67% | 26%
RTU-2 | DINING | 3000 | 3025 | 2200 | 2200 | 800 | 825 | 26.67% | 27.27%
RTU-3 | KITCHEN | 3600 | 3659 | 1080 | 1097 | 2520 | 2562 | 70% | 70.02%
RTU-4 | KITCHEN | 3600 | 3615 | 2520 | 2489 | 1080 | 1126 | 30% | 31.15%
EF-1 | KITCHEN HD | [10 empty] | 1995 | 2052
EF-2 | KITCHEN HD | [10 empty] | 1216 | 1260
EF-6 | RESTROOMS | [12 empty] | 300 | 307
TOTALS |  | 13200 | 13395 | 8000 | 8077 | 5200 | 5318 |  |  | 0 | 0 | 3211 | 3312 | 300 | 307
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 5200 | 5318 |  | FRONT |  | 0.059 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3511 | 3619 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 1689 | 1699 |  | REAR |  | 0.065 | [8 empty] | FALSE
[5 empty] | AVERAGE |  | 0.062
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0