## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 3400 | 3554 | 2800 | 2940 | 600 | 614 | 17.65% | 17.28%
RTU-2 | BACK OF HOUSE | 3400 | 3502 | 2800 | 2860 | 600 | 642 | 17.65% | 18.33%
KEF-1 | HOOD 1 | [10 empty] | 800 | 838
EF-1 | RESTROOM | [12 empty] | 100 | 105
EF-2 | WAREWASH | [12 empty] | 400 | 387
TOTALS |  | 6800 | 7056 | 5600 | 5800 | 1200 | 1256 |  |  | 0 | 0 | 800 | 838 | 500 | 492
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | TRUE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 1200 | 1256 |  | FRONT |  | 0.0016 | [8 empty] | FALSE | FALSE | TRUE
TOTAL EXHAUST |  | 1300 | 1330 |  | SIDE |  | 0.0002 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 0
NET AIRFLOW |  | -100 | -74 |  | REAR |  | 0.0003 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0007 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
BATHROOMS ARE OUTSIDE OF MAIN STRUCTURE CAUSING A NET POSITIVE IN BUILDING.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0