## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 9500 | 8779 | 7800 | 7116 | 1700 | 1663 | 17.89% | 44.08%
AC-2 | DINING A | 2500 | 3773 | 1975 | 3197 | 525 | 576 | 21% | 15.27%
AC-3 | DINING B | 4175 | 4337 | 3175 | 3371 | 1000 | 966 | 23.95% | 22.27%
AC-4 | DINING B | 2765 | 3196 | 2165 | 2539 | 600 | 657 | 21.7% | 20.56%
AC-5 | PLAY AREA | 1800 | 1887 | 1500 | 1581 | 300 | 306 | 16.67% | 16.22%
AC-6 | BOH | 1200 | 1258 | 1080 | 1133 | 120 | 125 | 10% | 9.936%
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1912 | 1948
EF-2 | HD3 | [10 empty] | 701 | 632
EF-3 | RESTROOM | [12 empty] | 500 | 516
EF-4 | HOOD 2 | [10 empty] | 701 | 642
TOTALS |  | 21940 | 14451 | 17695 | 18937 | 4245 | 4293 |  |  | 0 | 0 | 3314 | 3222 | 500 | 516
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4245 | 4293 |  | FRONT |  | 0.0036 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3814 | 3738 |  | SIDE |  | 0.0058 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 431 | 555 |  | REAR |  | 0.0074 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0056 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390