## VAV's
National TAB
Project: IBP 3481 - Quest
Address: 381 Plano Pkwy, Suite 100 The Colony, TX
Asset: Single Duct VAV's
Asset | Area Served | Address | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max)
VVT-1 | 107 | NA | VAV | 12" | 1560 | 1145 [1] | 312 | 529 | NA | NA | NA
VVT-2 | 101 | ADD31 | VAV | 12"X12" | 730 | 697 | 146 | 140 | NA | NA | NA
NOTES: [1] MOTORIZED DAMPER WAS FULLY OPEN DURING TIME OF TESTING.
Note on C7: NTAB: BILLINGSLEY ONLY

## VVT SGRD's
National TAB
Project: IBP 3481 - Quest
Address: 381 Plano Pkwy, Suite 100 The Colony, TX
Asset: VVT SGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design | Note
V1-1 | EXISTING OFFICE | CD | 10 | 260 | 182 | 182 | 0.7
V1-2 | EXISTING OFFICE | CD | 10 | 260 | 219 | 219 | 0.84231
V1-3 | EXISTING OFFICE | CD | 10 | 260 | 204 | 204 | 0.78462
V1-4 | EXISTING OFFICE | CD | 10 | 260 | 175 | 175 | 0.67308
V1-5 | EXISTING OFFICE | CD | 10 | 260 | 201 | 201 | 0.77308
V1-6 | EXISTING OFFICE | CD | 10 | 260 | 164 | 164 | 0.63077
VVT-1 |  |  |  | 1560 | 1145 | 1145 | 0.73397 | [1]
V2-1 | 100 | LD | 10 | 260 | 200 | 248 | 0.95385
V2-2 | 100 | LD | 10 | 230 | 154 | 227 | 0.98696
V2-3 | 101 | CD | 8 | 155 | 209 | 143 | 0.92258
V2-4 | 101 | LD | 6 | 85 | 139 | 79 | 0.92941
VVT-2 |  |  |  | 730 | 702 | 697 | 0.95479
NOTES: | [1] MOTORIZED DAMPER FULLY OPEN.

## AREA SGRD's
National TAB
Project: IBP 3481 - Quest
Address: 381 Plano Pkwy, Suite 100 The Colony, TX
Asset: AREA SGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design | Note
100-1 | 100 | CD | 8 | 200 | 185 | 185 | 0.925
100-2 | 100 | CD | 8 | 200 | 180 | 180 | 0.9
100-3 | 101 | CD | 8 | 200 | 183 | 183 | 0.915
VVT 100 | (EXISTING) |  |  | 600 | 548 | 548 | 0.91333
102-1 | 102 | CD | 10 |  | 303 | 303 |  | [1]
102-2 | 102 | CD | 10 |  | 310 | 310 |  | [1]
102-3 | 102 | CD | 10 |  | 320 | 320 |  | [1]
102-4 | 102 | CD | 10 |  | 319 | 319 |  | [1]
102-5 | 102 | CD | 10 |  | 235 | 235 |  | [1]
102-6 | 102 | CD | 10 |  | 230 | 230 |  | [1]
102-7 | 102 | CD | 10 |  | 316 | 316 |  | [1]
102-8 | 102 | CD | 10 |  | 279 | 279 |  | [1]
VVT 102 | (EXISTING) |  |  | 0 | 2312 | 2312
105-1 | 105 | CD | 10 |  | 206 | 206 |  | [1]
105-2 | 105 | CD | 10 |  | 309 | 309 |  | [1]
105-3 | 105 | CD | 10 |  | 162 | 162 |  | [1]
105-4 | 105 | CD | 10 |  | 204 | 204 |  | [1]
105-5 | 105 | CD | 10 |  | 207 | 207 |  | [1]
105-6 | 105 | CD | 10 |  | 287 | 287 |  | [1]
105-7 | 105 | CD | 10 |  | 229 | 229 |  | [1]
105-8 | 105 | CD | 10 |  | 263 | 265 |  | [1]
VVT 105 | (EXISTING) |  |  | 0 |  | 1869
107-1 | 107 | CD | 10 | 275 | 297 | 280 | 1.0182
107-2 | 107 | CD | 10 | 275 | 231 | 248 | 0.90182
107-3 | 107 | CD | 10 | 275 | 256 | 256 | 0.93091
107-4 | 107 | CD | 10 | 275 | 250 | 250 | 0.90909
107-5 | 107 | CD | 10 | 275 | 256 | 256 | 0.93091
107-6 | 107 | CD | 10 | 275 | 249 | 249 | 0.90545
VVT 107 | (EXISTING) |  |  | 1650 |  | 1539 | 0.93273
112-1 | 112 | CD | 8 | 75 | 78 | 78 | 1.04
112-2 | 112 | CD | 8 | 75 | 79 | 79 | 1.0533
VVT 112 | (EXISTING) |  |  | 150 | 157 | 157 | 1.0467
115-1 | 113 | S1 | 8 | 75 | 11 | 30 | 0.4 | [2]
115-2 | 115 | S1 | 8 | 100 | 25 | 28 | 0.28 | [2]
115-3 | 115 | S1 | 10 | 335 | 33 | 38 | 0.11343 | [2]
VVT 115 | (EXISTING)
114-1 | 114 | S1 | 8 | 75 | 177 | 72 | 0.96
NOTES: | [1] NO DESIGNS SHOWN PER PLANS.
[2] MOTORIZED DAMPER NOT FUNCTIONAL ON CALL FOR COOLING