## Report Sheet
STORE #: | 3566 | [22 empty] | Choose Yes or No: | SELECT FROM DROP DOWN LIST
CITY, STATE: | SHEFFIELD, OH | [22 empty] | Yes | 2 END PANEL - 171" HOOD LENGTH
HOOD TYPE: | 2 END PANEL - 156" HOOD LENGTH | [22 empty] | No | 2 END PANEL - 156" HOOD LENGTH
DATE: | 2023-05-23 | [23 empty] | 1 END PANEL (PLANHCA) - 156" HOOD LENGTH
TECH NAME: | DYLAN CRISMAN | [23 empty] | 1 END PANEL (PLANCHA) - 171" HOOD LENGTH
1 END PANEL (FRYER) - 156" HOOD LENGTH
1 END PANEL (FRYER) - 171" HOOD LENGTH
UNIT TAG |  |  | UNIT | AREA SERVED | INITIAL |  | FINAL |  | PULLEY CHANGE REQUIRED? | MOTOR RPM |  | FAN RPM |  | POWER
MFG | MODEL | S/N |  |  | DESIGN | INITIAL | GOAL | FINAL |  | INITIAL | FINAL | INITIAL | FINAL | HP | RLV (Initial) | RLV (Final) | PH | FLA | RLA(I) | RLA(F) | BHP(I) | BHP(F) | % Change
YORK | ZJ090N12D2B5HAA2A2 | N1G9098040 | RTU-1 | KITCHEN | 500 | 0 | 0 | 0 |  | 1749 | 1749 | 926 | 926 | 3 | 209.4 | 209.4 | 3 | 9.4 | 6.2 | 6.2 | 2.1703 | 2.1703 | 0%
YORK | ZJ102N8D2B5HAA2A2 | N1K9286795 | RTU-2 | DINING | 1000 | 0 | 1000 | 1025 |  | 1748 | 1748 | 915 | 915 | 3 | 209.1 | 209.1 | 3 | 9.4 | 6.8 | 6.8 | 2.3769 | 2.3769 | 0%
CAPTIVE AIRE | A1D.250-G10 | 4073262 | MUA-1 | HOOD 1 | 1775 | 1437 | 1500 | 1437 | No | 1778 | 1778 | 918 | 918 | 2 | 210.4 | 210.4 | 3 | 5.38 | 2.66 | 2.66 | 0.93555 | 0.93555 | 0%
CAPTIVE AIRE | NCA24HPFA | 4073262 | EF-1 | HOOD 1 | 2925 | 2012 | 2200 | 2012 | No | 1780 | 1780 | 779 | 779 | 3 | 210.1 | 210.1 | 3 | 5.68 | 2.8 | 2.8 | 0.98339 | 0.98339 | 0%
| RR FAN RUNNING? | Yes | EF-2 | RESTROOM | 150 | 150 | 150 | 150
NET BUILDING AIRFLOW CALCULATION
[5 empty] | DESIGN | INITIAL | GOAL | FINAL |  | FINAL B.P. | [5 empty] | ∆ Power | ∆ Load (CFM)
|  |  | TOTAL OA |  | 3275 | 1437 | 2500 | 2462 |  | FRONT DOOR |  | 0.0021 |  |  | INITIAL | 6.4661 | 1437
|  |  | TOTAL EXHAUST |  | 3075 | 2162 | 2350 | 2162 |  | BACK DOOR |  | 0.0016 |  |  | FINAL | 6.4661 | 2462
|  |  | NET AIRFLOW |  | 200 | -725 | 150 | 300 |  | AVERAGE |  | 0.00185 |  |  | ∆ | 0 | 1025
Issue List
Unit # | Description
EF-1 | EF / Hood Filters / Exhaust filters are dirty causing airflow to be low initially. Airflow could not be reduced. Recommend deep cleaning or replacement.
MUA-1 | MUA / Intake Filter / The intake air filter is dirty and had to temporarily be removed for testing. Recommend cleaning.
RTU-2 | RTU-2 Has 1 Alarm. Economizer Communication Failure. Economizer is not functional.
RTU-1 | RTU-1 Has 3 alarms. Economizer communication failure, C1 locked due to high pressure, C2 Locked to high pressure. Economizer not functional.
RTU-2 | OA Damper had to be manually set due to alarm. Set Damper position to 0.75" to obtain reading and marked.

## Issue list (hidden)
Select from drop down list
None
EF / Hood Filters / Exhaust filters are dirty causing airflow to be low initially. Airflow could not be reduced. Recommend deep cleaning or replacement.
MUA / Intake Filter / The intake air filter is dirty and had to temporarily be removed for testing. Recommend cleaning.
MUA / Not running / MUA is not running. Recommend servicing.
MUA / PSP / MUA is low and the PSP appears to be clogged. Unable to decrease MUA. Recommend cleaning.
RTU / Belt / Belt is broken and OA could not be tested.
RTU / Belt / Belt is loose and could not be tightened.
RTU / Filters / RTU filters are dirty. Temporarily removed for testing. Recommend replacement.
RTU / Not running / RTU is not running and could not be overriden on. Recommend servicing
RTU / OA Damper / Outside air damper is not functional and OA could not be set.
RTU / OA Filters / The outside air filters are dirty and had to be temporarily removed for testing. Recommend cleaning.
RTU / Rotation / Fan rotation is backwards. Unable to set OA. Recommend servicing.