## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 2000 | 1627 | 1600 | 1053 | 400 | 574 | 20% | 35.28%
RTU-2 | DINING | 2000 | 1467 | 1600 | 836 | 400 | 631 | 20% | 43.01%
RTU-3 | KITCHEN | 2400 | 2626 | 1920 | 2626 | 480 | 0 | 20% | 0%
MUA-1 | KITCHEN HD | [9 empty] | 614
KEF-1 | KITCHEN HD | [11 empty] | 1021
KEF-2 | KITCHEN HD | [11 empty] | 1516
EF-1 | MENS | [13 empty] | 204
EF-2 | WOMENS | [13 empty] | 235
TOTALS |  | 6400 | 5720 | 5120 | 4515 | 1280 | 1205 |  |  | 0 | 614 | 0 | 2537 | 0 | 439
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 1280 | 1819 |  | FRONT |  | -0.02 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 0 | 2976 |  | SIDE |  | -0.02 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 1280 | -1157 |  | REAR |  | -0.02 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.02 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SPEED CONTROLLER OR MUA IS NOT FUNCTIONING PROPERLY, FAN WILL ONLY SPIN AT LOW SPEED.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0