## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 3400 | 2554 | 3100 | 2067 | 300 | 487 | 8.824% | 19.07%
RTU-2 | DINNGER | 2400 | 3360 | 1900 | 3054 | 500 | 306 | 20.83% | 9.107%
MUA-1 | COOKLINE | [8 empty] | 1965 | 1911
KEF-1 | HOOD-1 | [10 empty] | 2275 | 2286
EF-2 | RESTROOMS | [12 empty] | 250 | 238
TOTALS |  | 5800 | 5914 | 5000 | 5121 | 800 | 793 |  |  | 1965 | 1911 | 2275 | 2286 | 250 | 238
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2765 | 2704 |  | FRONT |  | 0.0018 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2525 | 2524 |  | SIDE |  | - |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 240 | 180 |  | REAR |  | 0.0037 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.00275 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
RTU-1 has a 6 ton unit installed. RTU-2 has a 8.5 ton unit installed.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0