## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-4 | LIQUOR STORE | 1750 | 1717 | 1128 | 1036 | 622 | 681 | 35.54% | 39.66%
EF-4 | EMPLOYEE BREAK RM | [12 empty] | 150 | 143
EF-5 | LIQUORE STOCK RM | [12 empty] | 450 | 423
TOTALS |  | 1750 | 1717 | 1128 | 1036 | 622 | 681 |  |  | 0 | 0 | 0 | 0 | 600 | 566
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 622 | 681 |  | FRONT |  | 0.013
TOTAL EXHAUST |  | 600 | 566 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 22 | 115 |  | REAR
[5 empty] | AVERAGE |  | 0.013
NOTES: | [15 empty] | TRUE | FALSE | FALSE
[16 empty] | TRUE | FALSE | FALSE
TRUE