## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | REAR SALES | 3250 | 3264 | 2600 | 2613 | 650 | 651 | 20% | 19.94%
RTU-2 | FRONT SALES | 4875 | 5067 | 4150 | 4302 | 725 | 765 | 14.87% | 15.1%
RTU-3 | PHARMACY | 1600 | 1260 | 1360 | 1260 | 240 | 0 | 15% | 0%
RTU-4 | LIQUOR STORE | 1625 | 1717 | 1525 | 1036 | 100 | 681 | 6.154% | 39.66%
SF-1 | STOCK ROOM | [8 empty] | 2400
EF-1 | STOCK ROOM | [12 empty] | 2058 | 152
EF-2 | RESTROOMS | [12 empty] | 300 | 152
EF-3 | EMPLOYEE OFFICE | [12 empty] | 255 | 503
EF-4 | EMPLOYEE BREAK RM | [12 empty] | 110 | 143
EF-5 | LIQUORE STOCK RM | [12 empty] | 450 | 423
EF-6 | SALES | [12 empty] | 790 | 547
EF-7 | PHARMACY | [12 empty] | 750
TOTALS |  | 11350 | 11308 | 9635 | 9211 | 1715 | 2097 |  |  | 2400 | 0 | 0 | 0 | 4713 | 1920
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | TRUE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 4115 | 2097 |  | FRONT |  | 0.023" | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 4713 | 1920 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW:
NET AIRFLOW |  | -598 | 177 |  | REAR | [10 empty] | FALSE
AVERAGE
NOTES:
Liquor Store Pressure: Front- 0.0123