## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | RETAIL | 3400 | 3546 | 2900 | 3045 | 500 | 501 | 14.71% | 14.13%
RTU-2 | FOOD SERVICE | 4000 | 4011 | 3525 | 3537 | 475 | 474 | 11.88% | 11.82%
RTU-3 | RETAIL | 3000 | 2959 | 2750 | 2709 | 250 | 250 | 8.333% | 8.449%
EF-1 | RESTROOMS | [12 empty] | 325 | 303
EF-2 | FOOD SERVICE | [12 empty] | 400 | 406
TOTALS |  | 10400 | 10516 | 9175 | 9291 | 1225 | 1225 |  |  | 0 | 0 | 0 | 0 | 725 | 709
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 1225 | 1225 |  | FRONT |  | 0.0036 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 725 | 709 |  | SIDE |  | -0.0059 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 500 | 516 |  | REAR |  | 0.0042 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.00063333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0