## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 8125 | 8158 | 6375 | 6364 | 1750 | 1794 | 21.54% | 21.99%
AC-2 | MEAL FULFIL | 4375 | 4412 | 3300 | 3324 | 1075 | 1088 | 24.57% | 24.66%
AC-3 | DINNING/RR | 5250 | 5307 | 3975 | 4057 | 1275 | 1250 | 24.29% | 23.55%
AC-4 | BOH | 1750 | 1721 | 1325 | 1294 | 425 | 427 | 24.29% | 24.81%
AC-5 | PLAY AREA |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
AC-6 | BOH |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
EF-1 | HD 1 | [10 empty] | 1913 | 1768
EF-2 | HD 2 & 3 | [10 empty] | 1402 | 1336
EF-3 | RESTROOMS | [12 empty] | 300 | 304
EF4
EF 6 | RESTROOMS
TOTALS |  | 19500 | 19598 | 14975 | 15039 | 4525 | 4559 |  |  | 0 | 0 | 3315 | 3104 | 300 | 304
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4525 | 4559 |  | FRONT |  | 0.0078 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3615 | 3408 |  | SIDE |  | 0.0056 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 910 | 1151 |  | REAR |  | 0.0065 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0066333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390