## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AHU-1 | KITCHEN | 1380 | 1309 | 1195 | 1127 | 185 | 182 | 13.41% | 13.9%
AHU-2 | KITCHEN | 1380 | 1443 | 1195 | 1246 | 185 | 197 | 13.41% | 13.65%
AHU-3 | DINING | 1380 | 1466 | 930 | 1045 | 450 | 421 | 32.61% | 28.72%
EF-1 | HOT PREP | [12 empty] | 750 | 723
TOTALS |  | 4140 | 4218 | 3320 | 3418 | 820 | 800 |  |  | 0 | 0 | 0 | 0 | 750 | 723
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 820 | 800 |  | FRONT |  | 0.004 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 750 | 723 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 70 | 77 |  | REAR |  | 0.0031 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.00355 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0