## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AHU-4 | SPACE 470 | 900 | 916 | 700 | 713 | 200 | 203 | 22.22% | 22.16%
EF-1 | TRASH | [12 empty] | 100 | 92
TOTALS |  | 900 | 916 | 700 | 713 | 200 | 203 |  |  | 0 | 0 | 0 | 0 | 100 | 92
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 200 | 203 |  | FRONT |  | 0.003 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 100 | 92 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 100 | 111 |  | REAR | [10 empty] | TRUE
[5 empty] | AVERAGE |  | 0.003 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0