## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 3000 | 2932 | 2400 | 2310 | 600 | 622 | 20% | 21.21%
RTU-2 | SERVING | 3000 | 2813 | 2400 | 2186 | 600 | 627 | 20% | 22.29%
MUA-1 | KITCHEN | [8 empty] | 1650 | 1257
KEF-1 | HOOD1 | [10 empty] | 1120 | 1179
KEF-2 | HOOD2 | [10 empty] | 700 | 676
KEF-3 | HOOD3 | [10 empty] | 833 | 826
EF-1 | RESTROOM | [12 empty] | 75 | 78
EF-2 | RESTROOM | [12 empty] | 75 | 79
TOTALS |  | 6000 | 5745 | 4800 | 4496 | 1200 | 1249 |  |  | 1650 | 1257 | 2653 | 2681 | 150 | 157
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 2850 | 2506 |  | FRONT |  | -0.003 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 2803 | 2838 |  | SIDE |  | -0.002 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 47 | -332 |  | REAR |  | 0.001 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.0013333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SMOKE TEST WAS DONE WITH FOOD EQUIMPENT OFF BECAUSE STARTUPS ON FOOD SERVICE EQUIPMENT HAVE NOT BEEN CONDUCTED AT THAT TIME. GAS PIPING PREVENTED GRIDDLE FROM SITTING AGAINST THE BACK OF THE HOOD. INITIAL SMOKE TEST SHOWED THAT CAPTURE WAS AT 50%. TECHNICIAN ON SITE REDUCED MAU DESIGN FOR HOOD 1 SO THAT SMOKE CATURE WOULD BE 100%.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0