## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | ERV MAKE-UP |  | ERV EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AHU-1 | WAITING | 1130 | 1109 | 910 | 883 | 220 | 226 | 19.47% | 20.38%
AHU-2 | EXAM ROOMS | 742 | 786 | 592 | 647 | 150 | 139 | 20.22% | 17.68%
AHU-3 | BOH | 1177 | 1249 | 792 | 870 | 385 | 379 | 32.71% | 30.34%
AHU-4 | DENTAL | 318 | 297 | 268 | 245 | 50 | 52 | 15.72% | 17.51%
AHU-5 | SURGERY | 624 | 585 | 504 | 461 | 120 | 124 | 19.23% | 21.2%
ERV-1 | [9 empty] | 1075 | 1057 | 820 | 866
EF-1 | IT CLOSET | [12 empty] | 250 | 229
TOTALS |  | 3991 | 4026 | 3066 | 3106 | 925 | 920 |  |  | 1075 | 1057 | 820 | 866 | 250 | 229
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 1075 | 1057 |  | FRONT |  | -0.055 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 1070 | 1095 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 5 | -38 |  | REAR |  | -0.04 | [8 empty] | FALSE
[5 empty] | AVERAGE |  | -0.0475 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES:
[1] Building pressure is due to Highrise/neighboring tenant (laundromat) having negative pressure
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0