## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 5850 | 5974 | 4100 | 4287 | 1750 | 1687 | 29.91% | 28.24%
RTU-2 | KITCHEN | 6150 | 5907 | 4450 | 4121 | 1700 | 1786 | 27.64% | 30.24%
PRV-1 | RESTROOMS | [12 empty] | 375 | 384
PRV-2 | HD1 GRIDDLE | [10 empty] | 1500 | 1598
PRV-3 | HD2 FRYER | [10 empty] | 1500 | 1408
EF-1A | MOP ROOM | [12 empty] | 75 | 68
TOTALS |  | 12000 | 11881 | 8550 | 8408 | 3450 | 3473 |  |  | 0 | 0 | 3000 | 3006 | 450 | 452
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3450 | 3473 |  | FRONT |  | 0.003 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3450 | 3458 |  | SIDE |  | 0.006 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 0 | 15 |  | REAR |  | 0.002 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0036667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0