## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 9000 | 9088 | 7400 | 7532 | 1600 | 1556 | 17.78% | 17.12%
AC-2 | DINNING A /RR/ MECH | 2000 | 2004 | 1550 | 1570 | 450 | 434 | 22.5% | 21.66%
AC-3 | DRIVE THRU/ SERV/ DINNING | 4000 | 3919 | 3200 | 3109 | 800 | 810 | 20% | 20.67%
AC-4 | DINNING/ ENTRY/ ORDER | 4000 | 3969 | 3000 | 3004 | 1000 | 965 | 25% | 24.31%
AC-5 | PLAY AREA | 2000 | 2098 | 1700 | 1805 | 300 | 293 | 15% | 13.97%
AC-6 | BOH |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
EF-1 | HD 1 | [10 empty] | 1913 | 1780
EF-2 | HD 2 | [10 empty] | 701 | 663
EF-3 | RESTROOMS | [12 empty] | 300 | 320
EF-4 | HD 3 | [10 empty] | 701 | 706
EF-5 | RESTROOMS
TOTALS |  | 21000 | 21078 | 16850 | 17020 | 4150 | 4058 |  |  | 0 | 0 | 3315 | 3149 | 300 | 320
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4150 | 4058 |  | FRONT |  | 0.012 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3615 | 3469 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 535 | 589 |  | REAR |  | 0.012 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.012 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390