## Report Sheet
STORE #: | 3410 | [22 empty] | Choose Yes or No: | SELECT FROM DROP DOWN LIST
CITY, STATE: | Youngstown, OH. | [22 empty] | Yes | 2 END PANEL - 171" HOOD LENGTH
HOOD TYPE: | 2 END PANEL - 156" HOOD LENGTH | [22 empty] | No | 2 END PANEL - 156" HOOD LENGTH
DATE: | 2023-06-15 | [23 empty] | 1 END PANEL (PLANHCA) - 156" HOOD LENGTH
TECH NAME: | Dylan Crisman | [23 empty] | 1 END PANEL (PLANCHA) - 171" HOOD LENGTH
1 END PANEL (FRYER) - 156" HOOD LENGTH
1 END PANEL (FRYER) - 171" HOOD LENGTH
UNIT TAG |  |  | UNIT | AREA SERVED | INITIAL |  | FINAL |  | PULLEY CHANGE REQUIRED? | MOTOR RPM |  | FAN RPM |  | POWER
MFG | MODEL | S/N |  |  | DESIGN | INITIAL | GOAL | FINAL |  | INITIAL | FINAL | INITIAL | FINAL | HP | RLV (Initial) | RLV (Final) | PH | FLA | RLA(I) | RLA(F) | BHP(I) | BHP(F) | % Change
YORK | ZJ078N12B2B5HAA2A2 | N1C9744982 | RTU-1 | KITCHEN | 500 | 0 | 0 | 0 |  | 1739 | 1739 | 732 | 732 | 1.5 | 209.1 | 209.1 | 3 | 5 | 3.4 | 3.4 | 1.1884 | 1.1884 | 0%
YORK | ZJ090N18D2B5HAA2A2 | N1E9909942 | RTU-2 | DINING | 1000 | 1063 | 1000 | 1062 |  | 1748 | 1748 | 1024 | 1024 | 3 | 209.5 | 209.5 | 3 | 9.4 | 7.03 | 7.03 | 2.462 | 2.462 | 0%
CAPTIVE AIRE | A1-D.250-G10 | 3798149 | MUA-1 | HOOD 1 | 1775 | 607 | 1500 | 607 | No | 1781 | 1781 | 959 | 959 | 2 | 209.7 | 209.7 | 3 | 5.95 | 2.7 | 2.7 | 0.94646 | 0.94646 | 0%
CAPTIVE AIRE | NCA24HPFA | 3798149 | EF-1 | HOOD 1 | 2925 | 2697 | 2200 | 2245 | Yes | 1767 | 1778 | 858 | 727 | 2 | 210.9 | 209.7 | 3 | 5.95 | 3.5 | 2.9 | 1.2339 | 1.0166 | -17.61%
| RR FAN RUNNING? | Yes | EF-2 | RESTROOM | 150 | 150 | 150 | 150
NET BUILDING AIRFLOW CALCULATION
[5 empty] | DESIGN | INITIAL | GOAL | FINAL |  | FINAL B.P. | [5 empty] | ∆ Power | ∆ Load (CFM)
|  |  | TOTAL OA |  | 3275 | 1670 | 2500 | 1669 |  | FRONT DOOR |  | 0.0056 |  |  | INITIAL | 5.8308 | 1670
|  |  | TOTAL EXHAUST |  | 3075 | 2847 | 2350 | 2395 |  | BACK DOOR |  | -0.008 |  |  | FINAL | 5.6134 | 1669
|  |  | NET AIRFLOW |  | 200 | -1177 | 150 | -726 |  | AVERAGE |  | -0.0012 |  |  | ∆ | -0.21735 | -1
Issue List
Unit # | Description
MUA-1 | MUA / Intake Filter / The intake air filter is dirty and had to temporarily be removed for testing. Recommend cleaning.
MUA-1 | MUA / PSP / MUA is low and the PSP appears to be clogged. Unable to decrease MUA. Recommend cleaning.
RTU-2 | RTU-2 Is showing alarms for humidity temp sensors.
RTU-1 | RTU-1 Showing alarm for Indoor air quality temp sensor and economizer communication failure. damper closed, changed settings to 0 to remain closed.
Additional Notes:

## Issue list (hidden)
Select from drop down list
None
EF / Hood Filters / Exhaust filters are dirty causing airflow to be low initially. Airflow could not be reduced. Recommend deep cleaning or replacement.
EF / Not operational / The EF is not operational. Recommend servicing.
MUA / Intake Filter / The intake air filter is dirty and had to temporarily be removed for testing. Recommend cleaning.
MUA / Not operational / MUA is not operational. Recommend servicing.
MUA / PSP / MUA is low and the PSP appears to be clogged. Unable to decrease MUA. Recommend cleaning.
RTU / Belt / Belt is broken and OA could not be tested.
RTU / Belt / Belt is loose and could not be tightened.
RTU / Filters / RTU filters are dirty. Temporarily removed for testing. Recommend replacement.
RTU / Not running / RTU is not running and could not be overriden on. Recommend servicing
RTU / OA Damper / Outside air damper is not functional and OA could not be set.
RTU / OA Filters / The outside air filters are dirty and had to be temporarily removed for testing. Recommend cleaning.
RTU / OA Filters / OA filters are not installed. Recommend installing
RTU / Thermostats / Gridpoint stats are in Fan Auto. Recommend programming for Fan on except if kitchen RTU is balanced for 0 CFM OA.
RTU / Rotation / Fan rotation is backwards. Unable to set OA. Recommend servicing.