## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 3500 | 3539 | 3000 | 3018 | 500 | 521 | 14.29% | 14.72%
RTU-2 | DINING | 5250 | 5434 | 4250 | 4377 | 1000 | 1057 | 19.05% | 19.45%
MUA-1 | KITCHEN HOOD | [8 empty] | 1300 | 1294
EF-1 | KITCHEN HOOD | [10 empty] | 2550 | 2537
EF-2 | RESTROOM | [12 empty] | 150 | 153
TOTALS |  | 8750 | 8973 | 7250 | 7395 | 1500 | 1578 |  |  | 1300 | 1294 | 2550 | 2537 | 150 | 153
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2800 | 2872 |  | FRONT |  | 0.0078 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2700 | 2690 |  | SIDE |  | 0.006 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 100 | 182 |  | REAR | [10 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0069 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | CAPTIVE-AIRE |  | SOLO 9 16X16 |  |  |  | ACPSP |  | 165X9 |  | 1300 |  | 2550 |  | -1250