## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 2800 | 2702 | 2450 | 2343 | 350 | 359 | 12.5% | 13.29%
RTU-2 | KITCHEN | 3150 | 3294 | 2180 | 2302 | 970 | 992 | 30.79% | 30.12%
MUA-1 | COOKLINE | [8 empty] | 2030 | 2011
KEF-1 | HD1 | [10 empty] | 775 | 813
KEF-2 | HD2 | [10 empty] | 1763 | 1708
EF-1 | RESTROOMS | [12 empty] | 300 | 299
TOTALS |  | 5950 | 5996 | 4630 | 4645 | 1320 | 1351 |  |  | 2030 | 2011 | 2538 | 2521 | 300 | 299
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3350 | 3362 |  | FRONT |  | 0.0036 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2838 | 2820 |  | SIDE |  | 0.0045 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 512 | 542 |  | REAR | [10 empty] | TRUE
[5 empty] | AVERAGE |  | 0.00405 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
KITCHEN PRESSURIZATION (MUST BE NEGATIVE)
TOTALS |  | DESIGN | ACTUAL
TOTAL KITCHEN OA |  | 3000 | 3003
TOTAL KITCHEN EXHAUST |  | 2538 | 2521
NET AIRFLOW |  | 462 | 482
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0