## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | REAR KITCVHEN | 4000 | 4091 | 4000 | 3266 |  | 825 | 0% | 20.17%
RTU-2 | FRONT KITCHEN | 5000 | 3990 | 5000 | 3126 |  | 864 | 0% | 21.65%
RTU-3 | DINING | 4000 | 4023 | 4000 | 3194 |  | 829 | 0% | 20.61%
MUA-1 | HOOD | [9 empty] | 0
EF-1 | HOOD | [11 empty] | 2305
EF-2 | RESTROOMS | [11 empty] | 0
TOTALS |  | 13000 | 12104 | 13000 | 9586 | 0 | 2518 |  |  | 0 | 0 | 0 | 2305 | 0 | 0
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 0 | 2518 |  | FRONT |  | 0.013 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 0 | 2305 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 0 | 213 |  | REAR |  | 0.005 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.009 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
WIND CONSISTENTLY BLOWING ON SIDE DOOR, UNABLE TO GET ACCURATE PRESSURE ON THAT DOOR.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0