## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU1 |  | 2000 | 2003 | 2000 | 2003 |  | 0 | 0% | 0%
RTU2 |  | 1600 | 1627 | 1600 | 1627 |  | 0 | 0% | 0%
SF1 | [10 empty] | 2046
KEF-1 | [12 empty] | 1304
KEF-2 | [12 empty] | 1473
EF3 | [12 empty] | 862
CEF4 | [14 empty] | 71
CEF5 | [14 empty] | 72
TOTALS |  | 3600 | 3630 | 3600 | 3630 | 0 | 0 |  |  | 0 | 2046 | 0 | 3639 | 0 | 143
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 0 | 2046 |  | FRONT |  | -0.0317 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 0 | 3782 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 0 | -1736 |  | REAR | [10 empty] | FALSE
[5 empty] | AVERAGE |  | -0.0317 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0