## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 9500 | 9720 | 8020 | 8200 | 1480 | 1520 | 15.58% | 15.64%
AC-2 | DRIVE THRU | 5600 | 5261 | 4325 | 4078 | 1275 | 1183 | 22.77% | 22.49%
AC-3 | DINNING | 6400 | 5910 | 4375 | 4041 | 2025 | 1869 | 31.64% | 31.62%
AC-4 |  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
AC-5 |  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
AC-6 |  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1912 | 1893
EF-2 | HD2/HD3 FRYERS | [10 empty] | 1402 | 1412
EF-3 | RESTROOM | [12 empty] | 300 | 294
TOTALS |  | 21500 | 20891 | 16720 | 16319 | 4780 | 4572 |  |  | 0 | 0 | 3314 | 3305 | 300 | 294
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4780 | 4572 |  | FRONT |  | 0.0023 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3614 | 3599 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 1166 | 973 |  | REAR |  | 0.0092 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.00575 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390