## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 4000 | 3984 | 3200 | 3156 | 800 | 828 | 20% | 20.78%
RTU-2 | KITCHEN | 3400 | 3104 | 2800 | 2490 | 600 | 614 | 17.65% | 19.78%
EF-1 | HD1 PIZZA OVEN | [10 empty] | 900 | 901
EF-2 | RESTROOM | [12 empty] | 75 | 38
EF-3 | RESTROOM | [12 empty] | 75 | 51
EF-4 | ICE MACHINE | [12 empty] | 75 | 80
TOTALS |  | 7400 | 7088 | 6000 | 5646 | 1400 | 1442 |  |  | 0 | 0 | 900 | 901 | 225 | 169
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 1400 | 1442 |  | FRONT |  | 0.0006 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 1125 | 1070 |  | SIDE |  | 0.0004 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 275 | 372 |  | REAR |  | 0.0003 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.00043333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0