## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 2400 | 2474 | 1750 | 1823 | 650 | 651 | 27.08% | 26.31%
RTU-2 | KITCHEN | 3115 | 2928 | 2515 | 2283 | 600 | 645 | 19.26% | 22.03%
MUA-1 | HD 1 & HD 2 | [8 empty] | 1630 | 1635
KEF-1 | HD1 GRILL | [10 empty] | 1120 | 1108
KEF-2 | HD2 OVN | [10 empty] | 600 | 542
KEF-3 | HD 3 FRY | [10 empty] | 850 | 860
EF-4 | RESTROOM | [12 empty] | 75 | 82
EF-5 | RESTROOM | [12 empty] | 75 | 78
TOTALS |  | 5515 | 5402 | 4265 | 4106 | 1250 | 1296 |  |  | 1630 | 1635 | 2570 | 2510 | 150 | 160
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2880 | 2931 |  | FRONT |  | 0 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2720 | 2670 |  | SIDE |  | 0.0008 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 160 | 261 |  | REAR |  | 0.0001 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0003 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0