## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 9500 | 8927 | 7850 | 7306 | 1650 | 1621 | 17.37% | 18.16%
AC-2 | SERVING/DRIVE THRU | 5600 | 5459 | 4125 | 3932 | 1475 | 1527 | 26.34% | 27.97%
AC-3 | DINING | 5600 | 5390 | 4125 | 3903 | 1475 | 1487 | 26.34% | 27.59%
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1912 | 1944
EF-2 | HD2/HD3 FRYERS | [10 empty] | 1402 | 1449
EF-3 | RESTROOM | [12 empty] | 375 | 387
TOTALS |  | 20700 | 19776 | 16100 | 15141 | 4600 | 4635 |  |  | 0 | 0 | 3314 | 3393 | 375 | 387
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4600 | 4635 |  | FRONT |  | 0.0094 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3689 | 3780 |  | SIDE |  | 0.0072 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 911 | 855 |  | REAR |  | 0.0053 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0073 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390