## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 2950 | 2712 | 2700 | 2458 | 250 | 254 | 8.475% | 9.366%
RTU-2 | DINING | 4000 | 4003 | 3000 | 3033 | 1000 | 970 | 25% | 24.23%
MUA-1 | KITCHEN HOOD | [8 empty] | 1300 | 1411
EF-1 | KITCHEN HOOD | [10 empty] | 2400 | 2412
EF-2 | RESTROOM | [12 empty] | 150 | 158
TOTALS |  | 6950 | 6715 | 5700 | 5491 | 1250 | 1224 |  |  | 1300 | 1411 | 2400 | 2412 | 150 | 158
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2550 | 2635 |  | FRONT |  | 0.001 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2550 | 2570 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 0 | 65 |  | REAR |  | 0.001 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.001 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | CAPTIVE-AIRE |  | SOLO 9 16X16 |  |  |  | ACPSP |  | 165X9 |  | 1300 |  | 2550 |  | -1250