## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
F-7 | VESTIBLE/RR | 2000 | 1985 | 1535 | 1574 | 465 | 411 | 23.25% | 20.71%
F-8 | DINING/BAR | 2000 | 2034 | 1535 | 1603 | 465 | 431 | 23.25% | 21.19%
F-9 | KITCHEN | 2000 | 1970 | 1600 | 1558 | 400 | 412 | 20% | 20.91%
F-10 | KITCHEN | 2000 | 2035 | 1535 | 1574 | 465 | 461 | 23.25% | 22.65%
F-11 | KITCHEN | 2000 | 2084 | 1600 | 1661 | 400 | 423 | 20% | 20.3%
F-12 | DINING | 2000 | 1889 | 1535 | 1391 | 465 | 498 | 23.25% | 26.36%
HMUA | KITCHEN | [8 empty] | 3785 | 3497
KEF-1 | [13 empty] | 4390 | 4073
KEF-2 | [13 empty] | 1050 | 970
TOTALS |  | 12000 | 11997 | 9340 | 9361 | 2660 | 2636 |  |  | 3785 | 3497 | 0 | 0 | 5440 | 5043
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 6445 | 6133 |  | FRONT |  | 0.002 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 5440 | 5043 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 1005 | 1090 |  | REAR | [10 empty] | TRUE
[5 empty] | AVERAGE |  | 0.002 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0