## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 5200 | 5077 | 3200 | 3027 | 2000 | 2050 | 38.46% | 40.38%
RTU-2 | KITCHEN | 5000 | 4808 | 3000 | 2786 | 2000 | 2022 | 40% | 42.05%
PRV-2 | GRIDDLE | [10 empty] | 1500 | 1490
PRV-3 | FRYER | [10 empty] | 1500 | 1612
PRV-4 | DISH HOOD | [10 empty] | 350 | 355
EF-1 | RESTROOM | [12 empty] | 220 | 223
EF-2 | RESTROOM | [12 empty] | 50 | 48
EF-3 | RESTROOM | [12 empty] | 140 | 140
TOTALS |  | 10200 | 9885 | 6200 | 5813 | 4000 | 4072 |  |  | 0 | 0 | 3350 | 3457 | 410 | 411
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4000 | 4072 |  | FRONT |  | 0.01 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3760 | 3868 |  | SIDE |  | 0.011 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 240 | 204 |  | REAR |  | 0.009 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.01 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0