## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | Dining | 1750 | 1694 | 1400 | 1318 | 350 | 376 | 20% | 22.2%
RTU-2 | Dining | 1750 | 1734 | 1400 | 1380 | 350 | 354 | 20% | 20.42%
RTU-3 | Dining | 1750 | 1730 | 1400 | 1358 | 350 | 372 | 20% | 21.5%
RTU-4 | Kitchen | 1750 | 1714 | 1400 | 1340 | 350 | 374 | 20% | 21.82%
RTU-5 | Kitchen | 2625 | 2375 | 2130 | 1841 | 495 | 534 | 18.86% | 22.48%
EF-1 | Kitchen | [10 empty] | 2025 | 946
EF-2 | Kitchen | [10 empty] | 1615 | 2229
EF-3 | RR | [13 empty] | 119
TOTALS |  | 9625 | 9247 | 7730 | 7237 | 1895 | 2010 |  |  | 0 | 0 | 3640 | 3175 | 0 | 119
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | TRUE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 1895 | 2010 |  | FRONT |  | -0.0208 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 3640 | 3294 |  | SIDE |  | -0.0278 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | -1745 | -1284 |  | REAR |  | -0.0253 | [8 empty] | FALSE
[5 empty] | AVERAGE |  | -0.024633 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES:
INITIAL BUILDING PRESSURE FRONT DOOR -0.0726" SIDE DOOR -0.0747" BACK DOOR -0.0621"
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0