## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 6225 | 5742 | 4225 | 3657 | 2000 | 2085 | 32.13% | 36.31%
RTU-2 | KITCHEN | 6075 | 6416 | 4325 | 4583 | 1750 | 1833 | 28.81% | 28.57%
PRV-2 | GRIDDLE | [10 empty] | 1500 | 1490
PRV-3 | FRYER | [10 empty] | 1500 | 1482
PRV-1 | RESTROOM | [12 empty] | 375 | 407
EF-1A | MOP SINK | [12 empty] | 75 | 0
TOTALS |  | 12300 | 12158 | 8550 | 8240 | 3750 | 3918 |  |  | 0 | 0 | 3000 | 2972 | 450 | 407
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3750 | 3918 |  | FRONT |  | 0.0121 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3450 | 3379 |  | SIDE |  | 0.0139 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 300 | 539 |  | REAR |  | 0.0152 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.013733 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0