## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 8500 | 8207 | 6500 | 6226 | 2000 | 1981 | 23.53% | 24.14%
AC-2 | SIDE DINING | 2000 | 2132 | 1500 | 1624 | 500 | 508 | 25% | 23.83%
AC-3 | MAIN DINING | 4000 | 4097 | 3100 | 3163 | 900 | 934 | 22.5% | 22.8%
AC-4 | MAIN DINING | 3400 | 2385 | 2600 | 1831 | 800 | 554 | 23.53% | 23.23%
AC-5 | MAIN DINING | 1200 | 1296 | 900 | 989 | 300 | 307 | 25% | 23.69%
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1912 | 1887
EF-2 | HD2/HD3 FRYERS | [10 empty] | 1402 | 1449
EF-3 | RESTROOM | [12 empty] | 350 | 0
TOTALS |  | 19100 | 18117 | 14600 | 13833 | 4500 | 4284 |  |  | 0 | 0 | 3314 | 3336 | 350 | 0
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4500 | 4284 |  | FRONT |  | 0.0144 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3664 | 3336 |  | SIDE |  | 0.0152 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 836 | 948 |  | REAR |  | 0.0072 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.012267 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390