## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
FCU-1 | DINING | 1900 | 1996 | 1250 | 1250 | 650 | 688 | 34.2% | 34.47%
FCU-2 | KITCHEN | 4400 | 4503 | 4400 | 0 | 0 | 0 | 0% | 0%
FCU-3 | DISPLAY RM | 900 | 1025 | 900 | 1025 | 0 | 0 | 0% | 0%
FCU-4 | MGRS OFFICE |  |  |  |  | 40 | 41 | - | -
MUA-1 | COOKLINE | [8 empty] | 1700 | 1682
SF1 | FCU1&4 OA |  |  |  |  | 690 | 729 | - | -
ESP-1 | HOODS 1/2 | [10 empty] | 2500 | 2605
EF-1 | TOILETS | [12 empty] | 75 | 71
TOTALS |  | 7200 | 7524 | 6550 | 2275 | 1380 | 1458 |  |  | 1700 | 1682 | 2500 | 2605 | 75 | 71
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3080 | 3140 |  | FRONT | [10 empty] | #DIV/0! | #DIV/0! | FALSE
TOTAL EXHAUST |  | 2575 | 2676 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | #DIV/0!
NET AIRFLOW |  | 505 | 464 |  | REAR | [10 empty] | #DIV/0!
[5 empty] | AVERAGE |  | #DIV/0! |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | #DIV/0!
KITCHEN PRESSURIZATION (MUST BE NEGATIVE)
TOTALS |  | DESIGN | ACTUAL
TOTAL KITCHEN OA |  | 1700 | 1682
TOTAL KITCHEN EXHAUST |  | 2500 | 2605
NET AIRFLOW |  | -800 | -923
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0