CARVE – Austin, TX Commissioning Plan & Procedures

Our team will review job specifications & plans to develop the commissioning process & criteria for the disciplines outline for review & input from design & construction teams. The criteria will consist of the following:

- Work  with the construction team to develop a working schedule for each of the commissioning process in relationship with the actual construction schedule.

- Provide direction and support to use the FaciliBuild HUB Digital Platform (IOS and Android application), National TAB  will utilize to provide easy access to perform each onsite commissioning task. The platform allows our team and other trade team members to have access to:

  - Portal to all team members for easy access to contact info & who’s who.

  - Organized area for all related files & documents in respect to commissioning

  - Digital Checklist that are critical to commissioning process to document pass/fail test data  and visual validation. The Checklist modules is where all FIV, OPT, & FPT test for each commissioning activity.

  - Field Issues/RFI module that can be assigned to the required team member to address.

  - Provide final digital and hard copy reports of specific commissioning activity immediately & a final complete report at the end of the project.

- An introduction of the commissioning process to lead team member for each discipline stated above for coordination & review of the commissioning process for their specific discipline. The commissioning team will work with each member individually to gather input & expertise of each trades discipline to finalize all field checklist with respect to asset/systems provided and current construction conditions.

- Each discipline commissioned will consist of a commissioning procedure that includes the activities to be performed. The commissioning team will provide notice prior to any test of the participants required during each of the commissioning process.  Construction team shall ensure all manufacturer’s submittals, construction team contacts, design documents shall be made available for review to assist in commissioning procedure development. A review of the commissioning plan shall be performed by all involved trades to ensure their role in the process and to verify that no specific test points are left out of functional testing.

- Preliminary Pre-Commissioning walk-through:  NT Commissioining team will schedule a walk through with each trade to conduct a preliminary inspection prior to final testing.  The walk-through will validate installation is complete and proper, power supply, control wiring along with normal and abnormal interlocks.  Any failed observations will require immediate resolution prior to commencing OPT and FPT testing.

- Document & perform or witness Functional Installation Verfications (FIV), Operational Performance Test (OPT), and Functional Performance Test (FPT) for each system or asset being commissioned. FIV consist of the inspection of the installation of assets and systems. OPT are operational inspections and in most cases are the asset startup reports performed by the associated trade or manufacture. FPT are the critical point to point testing of each system input vs output. FPT also ensures there is a positive relationship and cohesiveness between each associated system and the building itself which will enturn provide a healthy building with comfort under control.

- Reporting of deficiencies & documentation of walk-throughs, pass-fail testing shall be provided immediately to the team with action steps needed from the team to facilitate additional testing if required.

- Final digital & hard copy Commissioning report shall be submitted to team with the following, but not limited, to an executive summary, completed walk-through & testing checklist, and functional pass/fail reports. Other required trades must also include all TAB reports, DALT testing reports, specific equipment & manufacturers startups & warranty documents to be included in the report as references to the final Commissioning documentation.

Commissioning Management Team & Responsibilities for key team members

Dan Hertenstein, NEBB Professional will manage the overall commissioning process. Provide technical expertise to carry out the commissioning plan and assist entire team to a positive solutions for any issues that arrive. Dan will also provide periodic summary of completed work, modification of commissioning schedule, changes to any testing criteria, manage team work plan.

Will Turnbough, NEBB Professional will assist Dan in management of the commissioning process, and review the TAB reports.

Wesley John (BS-Engineering), Will pefrom on-site commissioning test completing the required checklist, and assign issues to team members as they are discovered.

Brian Turnbough:  Will lead the communication plan to ensure team members have access to our platform and assist our internal & external teams with the collaboration and ensure all activites are performed in a timely and expedient manner.

Brianna Biggs, Will maintain all required documentation which consist of but not limited to ensuring commissioning team has the latest documentations for each discipline,

External Team Members

Design Team Members, shall be available to communicate electronically or verbally on a as needed basis to provide clarity of design intent and assist with commissioning issues

General Contractor & PM’s, Ensure the integration and development of all construction schedules with commissioning schedules. Keeps commissioning informed of completion of specific assets or system in a timely fashon to allow the commissioning team to schedule with trades for task required. Ensure all trades provide proper startup documents. Ensure that all trades and the commissioning teams are communicating properly for a successful outcome.

Site Trades (MC, EC, TAB, PC, SPECIALTY), Must perform or assist in all FIV, OPT, FPT developed for their respective trade. Attend meetings and assist of resolution of any issues until satisfactory. Support the GC & Commissioning team of proper timing of commissioning activities required. Each trade shall review initial site checklist with commissioning team to ensure proper testing parameters are selected are feasible based upon design & current construction conditions. Controls & Fire Systems will be required to provide documentation of point-to-point test that systems are communicating and trend logs during FPT testings as needed by all team members.

Various external team members will be requested to witness of critical FPT testing which would consist the trade discipline, commissioning member, general contractors project manager, and possibly a member of design team when need to ensure FPT is meeting the design SOO and parameters.

Several FIV & OPT may refer to previous Installation Validation reports provided or startup reports performed by trades/GC of various assets or systems prior to the commissioning mobilization to the site or deemed simplicity in nature with no controls or critical sequencing.

Commissioning Team Procedures:

The various system commissioning will encompass the Mechanical, TAB, Controls, Electrician, Plumbing and Specialty contractors to assist when needed on all site walk-thru and testing. All check-out startup documents are required prior to commencing on various OPT & all FPT Test. The lead for the mechanical contractor shall provide insight & direction of testing points to the commissioning team.

Commissioning Procedures:

Testing will follow planned control, SOO, and Performance criteria.  If any failures occur, the associated trades must resolve & be present for retesting of each previously failed test. Full-load, normal operation load conditions will be performed on all major assets. System-to-system interfacing relationships will be evaluated & tested in conjunction with building pressurization flow requirements.

- Verify schedules and setpoints are programmed (Occupied & Unoccupied times)

Seasonal Testing

Initial report will include phase I test reporting.  Additional test will be conducted in the following season to show change of climate conditions and control management.  In addition following season test shall take into account initial and current building performance and function to ensure operational behaviour is inline with results of testing conducted. Should operational issues arise, commissioning agent shall validate and retest these components as a assurance of equipment and system FOP.

Next Test shall be conducted October 2023