## DOAS-1
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: DOAS-1 |  | Area: SURGERY |  |  |  | SUBMITTAL
Unit Data |  |  | Test Data |  |  | RETURN FAN | NA
Manufacturer | TRANE |  |  | Design | Actual | 4" ANGLE FILTER | SECTION 1
Model Number | CSAA030UA |  | Total CFM | 13000 |  | HW COIL | SECTION 2
Serial Number |  |  | Fan RPM |  |  | SUPPLY FAN | SECTION 5
Configuration | VERTICAL |  | VFD Speed |  |  | CHW COIL | SECTION 8
No. Final Filters / Size | 3 / 12X24X4 |  | RL Voltage | 460
No. Final Filters / Size | 2 / 16X20X4 |  | RL Amperage
No. Final Filters / Size | 6 / 20X24X4 |  | Motor B.H.P. | 2@7.5
Performance Data
|  |  |  | Design | Actual
System Set Point
Motor Data |  |  | Suction S.P.
Motor MFG / Frame |  |  | Discharge S.P.
Horsepower / RPM | 2@25.0 / 2@1800 |  | Total SP | 4.714
Rated Volts / Phase | 460 / 3 |  | CW Coil P.D. |  |  | CHW COIL GPM | 201.8
Rated Amperage / SF |  |  | HW Coil P.D. |  |  | HW COIL GPM | 32.1
Final Filters P.D.
Heat Wheel P.D.
Pre Filters P.D.
|  |  | Total ESP | 0.5

## AHU-G-1
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: AHU-G-1 |  | Area: GENERAL |  |  |  | SUBMITTAL
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data |  |  | RETURN FAN | SECTION 4
Manufacturer | TRANE |  | Manufacturer |  |  | 4" ANGLE FILTER | SECTION 5
Model Number | CSAA050UA |  | Model Number |  |  | HW COIL | SECTION 6
Serial Number |  |  | Serial Number |  |  | CHW COIL | SECTION 8
Configuration | VERTICAL |  | Configuration | VERTICAL |  | SUPPLY FAN | SECTION 11
No. Pre Filters / Size | 36 / 20x20x4 |  | No. Pre Filters / Size |  |  | 12" BAG FILTER | SECTION 12
No. Final Filters / Size | 5 / 12x24x12
No. Final Filters / Size | 10 / 24x24x12
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | / 4@1800 |  | Horsepower / RPM | / 4@1800
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF |  |  | Rated Amperage / SF
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 21900 |  | Total CFM | 13450
Min OA CFM | 7550
Fan RPM | 3290 |  | Fan RPM | 1803
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage |  |  | RL Amperage
Motor B.H.P. | 48.085 |  | Motor B.H.P. | 7.642
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 9.097 |  | Total SP | 2.145
CW Coil P.D. | 0.796 |  |  |  |  | CHW COIL GPM | 157.32
HW Coil P.D. | 0.013 |  |  |  |  | HW COIL GPM | 18.97
HW Coil P.D.
System Set Point
Pre Filters P.D.
Pre Filters P.D.
Total ESP | 4.4 |  | Total ESP | 1.1

## AHU-G-1 VAV's (1)
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: AHU-G-1 VAV's | [10 empty] | SUBMITTAL
Asset | Area Served | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max) | HW COIL GPM
ATU-G-1-01 | H.01L02 | HEAT | 8 | 650 |  | 165 |  | 575 |  |  | 2.48
ATU-G-1-02 | H.0117 | HEAT | 16 | 1800 |  | 820 |  | 900 |  |  | 1.71
ATU-G-1-03 | H.0119 | HEAT | 6 | 150 |  | 40 |  | 95 |  |  | 0.16
ATU-G-1-04 | H.01C02 | HEAT | 8 | 650 |  | 430 |  | 430 |  |  | 1.25
ATU-G-1-05 | H.0101 HALL | HEAT | 8 | 600 |  | 215 |  | 300 |  |  | 0.68
ATU-G-1-06 | H.0101 | HEAT | 8 | 300 |  | 85 |  | 150 |  |  | 0.27
ATU-G-1-07 | H.0107 | HEAT | 8 | 600 |  | 145 |  | 300 |  |  | 0.68
ATU-G-1-08 | H.00C01 | HEAT | 6 | 250 |  | 150 |  | 150 |  |  | 0.31
ATU-G-1-09 | H.01C04 | HEAT | 10 | 1100 |  | 630 |  | 1000 |  |  | 3.28
ATU-G-1-10 | H.0114 | HEAT | 8 | 500 |  | 120 |  | 250 |  |  | 0.51
ATU-G-1-11 | H.0112 | HEAT | 10 | 1000 |  | 125 |  | 500 |  |  | 1.18
ATU-G-1-12 | H.01C02 | HEAT | 8 | 700 |  | 400 |  | 400 |  |  | 1.09
ATU-G-1-13 | H.0404 | HEAT | 8 | 650 |  | 390 |  | 390 |  |  | 1.03
ATU-G-1-14 | H.0415 | HEAT | 10 | 1000 |  | 1000 |  | 1000 |  |  | 3.28
ATU-G-1-15 | H.0423 | HEAT | 8 | 300 |  | 0 |  | 150 |  |  | 0.27
ATU-G-1-16 | H.0424 | HEAT | 8 | 700 |  | 90 |  | 350 |  |  | 0.86
ATU-G-1-17 | H.0427 | HEAT | 8 | 700 |  | 375 |  | 425 |  |  | 2.63
ATU-G-1-18 | H.0422 | HEAT | 8 | 650 |  | 115 |  | 325 |  |  | 1.31
ATU-G-1-19 | H.0417 | HEAT | 8 | 550 |  | 480 |  | 480 |  |  | 1.98
ATU-G-1-20 | H.04E01 | HEAT | 8 | 550 |  | 0 |  | 275 |  |  | 0.59
ATU-G-1-21 | H.04C02 | HEAT | 6 | 200 |  | 50 |  | 100 |  |  | 0.25
ATU-G-1-22 | H.0413 | HEAT | 6 | 250 |  | 90 |  | 155 |  |  | 0.46
ATU-G-1-23 | H.0414 | HEAT | 10 | 900 |  | 395 |  | 460 |  |  | 0.66
ATU-G-1-24 | H.0407 | HEAT | 8 | 400 |  | 400 |  | 400 |  |  | 1.09
ATU-G-1-25 | H.0409 | HEAT | 8 | 300 |  | 90 |  | 150 |  |  | 0.27
ATU-G-1-26 | H.0410 | HEAT | 8 | 650 |  | 85 |  | 325 |  |  | 1.31
ATU-G-1-27 | H.0320 | HEAT | 8 | 650 |  | 170 |  | 645 |  |  | 4.12
ATU-G-1-28 | H.03T01 |  | 14 | 1700 |  | 0 |  | 850 |  |  | 1.72
ATU-G-1-29 | H.03M01 | HEAT | 14 | 1700 |  | 0 |  | 850 |  |  | 2.68
|  |  |  | 20150 | 0 |  |  | 12380 | 0
Note on C7: NTAB: BILLINGSLEY ONLY

## AHU-G-1 VAV's (2)
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: AHU-G-1 VAV's | [10 empty] | SUBMITTAL
Asset | Area Served | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max) | HW COIL GPM
ATU-G-1-30 | H.03E01 |  | 12 | 1400 |  | 0 |  | 700 |  |  | 1.64
ATU-G-1-31 | H.0301 | HEAT | 6 | 250 |  | 0 |  | 125 |  |  | 0.34
ATU-G-1-32 | H.0321 | HEAT | 6 | 100 |  | 0 |  | 50 |  |  | 0.24
|  |  |  | 1750 | 0 |  |  | 875 | 0
TOTAL |  |  |  | 21900 | 0 |  |  | 13255 | 0
Note on C7: NTAB: BILLINGSLEY ONLY

## AHU-G-2
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: AHU-G-2 |  | Area: LAB & PHARMACY |  |  |  | SUBMITTAL
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data |  |  | RETURN FAN | SECTION 3
Manufacturer | TRANE |  | Manufacturer |  |  | 4" ANGLE FILTER | SECTION 5
Model Number | CSAA030UA |  | Model Number |  |  | HW COIL | SECTION 6
Serial Number |  |  | Serial Number |  |  | CHW COIL | SECTION 8
Configuration | VERTICAL |  | Configuration | VERTICAL |  | SUPPLY FAN | SECTION 11
No. Pre Filters / Size | 18 / 16x20x4 |  | No. Pre Filters / Size |  |  | 12" BAG FILTER | SECTION 12
No. Pre Filters / Size | 6 / 16x25x4
No. Final Filters / Size | 3 / 12x24x12
No. Final Filters / Size | 8 / 20x20x12
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | / 4@3600 |  | Horsepower / RPM | / 2@1200
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF |  |  | Rated Amperage / SF
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 12950 |  | Total CFM | 6150
Min OA CFM | 7850
Fan RPM | 3624 |  | Fan RPM | 1500
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage |  |  | RL Amperage
Motor B.H.P. | 65.32 |  | Motor B.H.P. | 63.03
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 8.594 |  | Total SP | 2.237
CW Coil P.D. | 0.796 |  |  |  |  | CHW COIL GPM | 131.2
HW Coil P.D. | 0.013 |  |  |  |  | HW COIL GPM | 19.38
HW Coil P.D.
System Set Point
Pre Filters P.D.
Pre Filters P.D.
Total ESP | 3.6 |  | Total ESP | 1.0

## AHU-G-2 Valves (1)
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
ALL MARKED ON GRD
Asset: AHU-G-2 Air Valves | [10 empty] | SUBMITTAL
Asset | Area Served | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max) | HW COIL GPM
SAV-G-2-01 | H.0201 | REHEAT | 6 | 300 |  | 80 |  | 150 |  |  | 0.6
SAV-G-2-02 | H.0215 | REHEAT | 18 | 2900 |  | 1101 |  | 1450 |  |  | 5.9
SAV-G-2-03 | H.0218 | REHEAT | 8 | 600 |  | 126 |  | 300 |  |  | 1.3
SAV-G-2-04 | H.0213 | REHEAT | 14 | 1400 |  | 450 |  | 700 |  |  | 3
SAV-G-2-05 | H.0209 | REHEAT | 10 | 800 |  | 220 |  | 400 |  |  | 1.7
SAV-G-2-06 | H.0211 | REHEAT | 8 | 600 |  | 180 |  | 300 |  |  | 1.3
SAV-G-2-07 | H.0319 | REHEAT | 6 | 350 |  | 145 |  | 175 |  |  | 0.9
SAV-G-2-08 | H.0315 | REHEAT | 16 | 2100 |  | 576 |  | 1050 |  |  | 4.2
SAV-G-2-09 | H.0312 | REHEAT | 10 | 1000 |  | 240 |  | 500 |  |  | 2
SAV-G-2-10 | H.0311 | REHEAT | 10 | 900 |  | 900 |  | 900 |  |  | 3.5
SAV-G-2-11 | H.0309 | REHEAT | 4 | 150 |  | 48 |  | 75 |  |  | 0.3
SAV-G-2-12 | H.0307 | REHEAT | 8 | 600 |  | 126 |  | 300 |  |  | 1.3
SAV-G-2-13 | H.0204 | REHEAT | 10 | 750 |  | 210 |  | 375 |  |  | 1.6
SAV-G-2-14 | H.0310 | REHEAT | 8 | 500 |  | 500 |  | 500 |  |  | 2
AHU-G-2 SAV |  |  |  | 12950 | 0 |  |  | 7175 | 0
RAV-G-2-01 | H.0201 | RETURN | 4 | 100 |  | 40
RAV-G-2-03 | H.0218 | RETURN | 7 | 500 |  | 125
RAV-G-2-07 | H.0319 | RETURN | 6 | 250 |  | 90
RAV-G-2-08 | H.0318 | RETURN | 12 | 1900 |  | 380
RAV-G-2-09 | H.0313 | RETURN | 8 | 900 |  | 180
RAV-G-2-10 | H.0311 | RETURN | 9 | 1000 |  | 200
RAV-G-2-11 | H.0309 | RETURN | 4 | 150 |  | 40
RAV-G-2-12 | H.0307 | RETURN | 7 | 600 |  | 130
RAV-G-2-14 | H.0310 | RETURN | 7 | 500 |  | 125
AHU-G-2 RAV |  |  |  | 5900 | 0
Note on C7: NTAB: BILLINGSLEY ONLY

## AHU-G-2 Valves (2)
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
ALL MARKED ON GRD
Asset: AHU-G-2 Air Valves | [10 empty] | SUBMITTAL
Asset | Area Served | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max)
EAV-G-2-01 | H.0308 | EXHAUST | 4 | 100 |  | 40 |  |  |  |  | EF-ISO-2A & 2B
EAV-G-2-02A | H.0215 | EXHAUST | 10 | 1300 |  | 260 |  |  |  |  | EF-ISO-2A & 2B
EAV-G-2-02B | H.0215 | EXHAUST | 10 | 1300 |  | 260 |  |  |  |  | EF-ISO-2A & 2B
EAV-G-2-02C | H.0215 | EXHAUST | 7 | 700 |  | 140 |  |  |  |  | EF-ISO-2A & 2B
EAV-G-2-04 | [1] | EXHAUST | 10 | 1300 |  | 260
EAV-G-2-05 | H.0209 | EXHAUST | 8 | 800 |  | 160 |  |  |  |  | EF-ISO-2A & 2B
EAV-G-2-06 | H.0211 | EXHAUST | 7 | 500 |  | 125 |  |  |  |  | EF-ISO-2A & 2B
EAV-G-2-07 | H.0319 | EXHAUST | 4 | 100 |  | 40 |  |  |  |  | EF-ISO-2A & 2B
EAV-G-2-13 | H.0204 | EXHAUST | 8 | 850 |  | 170 |  |  |  |  | EF-ISO-2A & 2B
RTU-G-2 EAV |  |  |  | 6950 | 0
NOTES: | [1] LISTED IN SCHEDULE, NOT MARKED ON DRAWING.
Note on C7: NTAB: BILLINGSLEY ONLY

## AHU-G-3
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: AHU-G-3 |  | Area: DIETARY |  |  |  | SUBMITTAL
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data |  |  | RETURN FAN | SECTION 3
Manufacturer | TRANE |  | Manufacturer |  |  | 4" ANGLE FILTER | SECTION 5
Model Number | CSAA080UA |  | Model Number |  |  | HW COIL | SECTION 6
Serial Number |  |  | Serial Number |  |  | CHW COIL | SECTION 8
Configuration | VERTICAL |  | Configuration | VERTICAL |  | SUPPLY FAN | SECTION 11
No. Pre Filters / Size | 8 / 16X20X4 |  | No. Pre Filters / Size |  |  | 12" BAG FILTER | SECTION 12
No. Pre Filters / Size | 48 / 20X20X4
No. Final Filters / Size | 4 / 24X12X12
No. Final Filters / Size | 20 / 24X24X12
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | / 4@1800 |  | Horsepower / RPM | / 4@1200
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF |  |  | Rated Amperage / SF
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 36750 |  | Total CFM | 21000
Min OA CFM | 16400
Fan RPM | 2310 |  | Fan RPM | 1238
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage |  |  | RL Amperage
Motor B.H.P. | 67.74 |  | Motor B.H.P. | 8.414
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 8.157 |  | Total SP | 1.580
CW Coil P.D. | 0.939 |  |  |  |  | CHW COIL GPM | 303.82
HW Coil P.D. | 0.014 |  |  |  |  | HW COIL GPM | 48.83
HW Coil P.D.
System Set Point
Pre Filters P.D.
Pre Filters P.D.
Total ESP | 4.0 |  | Total ESP | 1.1

## AHU-G-3 VAV's
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: AHU-G-3 VAV's | [10 empty] | SUBMITTAL
Asset | Area Served | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max) | HW COIL GPM
ATU-G-3-01 | H.0001 | HEAT | 8 | 450 |  | 450 |  | 450 |  |  | 1.37
ATU-G-3-02 | H.0002 | HEAT | 10 | 1000 |  | 645 |  | 655 |  |  | 4.35
ATU-G-3-03 | H.0005 | HEAT | 6 | 400 |  | 365 |  | 365 |  |  | 1.29
ATU-G-3-04 | H.0007 | HEAT | 12 | 1400 |  | 340 |  | 700 |  |  | 2.83
ATU-G-3-05 | H.0007 | HEAT | 12 | 1300 |  | 275 |  | 650 |  |  | 2.42
ATU-G-3-06 | H.0005 | HEAT | 16 | 2600 |  | 1025 |  | 1300 |  |  | 2.93
ATU-G-3-07 | H.0008 | HEAT | 16 | 2100 |  | 345 |  | 1050 |  |  | 2.12
ATU-G-3-08 | H.0008 | HEAT | 16 | 2400 |  | 220 |  | 1200 |  |  | 2.58
ATU-G-3-09 | H.0008 | HEAT | 16 | 2700 |  | 0 |  | 1350 |  |  | 3.11
ATU-G-3-10 | H.0008 | HEAT | 12 | 1400 |  | 0 |  | 700 |  |  | 1.64
ATU-G-3-11 | H.0009 | HEAT | 14 | 1700 |  | 0 |  | 850 |  |  | 1.72
ATU-G-3-12 | H.0013 | HEAT | 10 | 1100 |  | 260 |  | 550 |  |  | 1.38
ATU-G-3-13 | H.0014 | HEAT | 10 | 900 |  | 195 |  | 450 |  |  | 1.64
ATU-G-3-14 | H.0014 | HEAT | 16 | 1800 |  | 170 |  | 900 |  |  | 1.71
ATU-G-3-15 | H.0014 | HEAT | 16 | 1800 |  | 175 |  | 900 |  |  | 1.71
ATU-G-3-16 | H.0015 | HEAT | 8 | 350 |  | 0 |  | 175 |  |  | 0.33
ATU-G-3-17 | HOOD #2 | HEAT | 16 | 2400 |  | 0 |  | 1200 |  |  | 2.58
ATU-G-3-18 | H.0014 | HEAT | 16 | 2300 |  | 0 |  | 1150 |  |  | 2.42
ATU-G-3-19 | H.0023 | HEAT | 8 | 700 |  | 100 |  | 350 |  |  | 1.53
ATU-G-3-20 | H.0014 | HEAT | 12 | 1400 |  | 145 |  | 700 |  |  | 1.64
ATU-G-3-21 | H.0022 | HEAT | 6 | 200 |  | 80 |  | 100 |  |  | 0.25
ATU-G-3-22 | H.0014 | HEAT | 16 | 2000 |  | 170 |  | 1000 |  |  | 1.97
ATU-G-3-23 | H.0021 | HEAT | 8 | 350 |  | 140 |  | 175 |  |  | 0.33
ATU-G-3-24 | H.03C01 | HEAT | 8 | 400 |  | 70 |  | 200 |  |  | 0.38
ATU-G-3-25 | H.0014 | HEAT | 24X16 | 3600 |  | 0 |  | 1800 |  |  | 3.43
|  |  |  | 36750 | 0 |  |  | 18920 | 0
Note on C7: NTAB: BILLINGSLEY ONLY

## AHU-1-1
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: AHU-1-1 |  | Area: SURGERY |  |  |  | SUBMITTAL
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data |  |  | RETURN FAN | SECTION 3
Manufacturer | TRANE |  | Manufacturer |  |  | 4" ANGLE FILTER | SECTION 5
Model Number | CSAA035UA |  | Model Number |  |  | HW COIL | NA
Serial Number |  |  | Serial Number |  |  | CHW COIL | SECTION 9
Configuration | VERTICAL |  | Configuration | VERTICAL |  | SUPPLY FAN | SECTION 12
No. Pre Filters / Size | 6 / 16X20X4 |  | No. Pre Filters / Size |  |  | 12" BAG FILTER | SECTION 13
No. Pre Filters / Size | 18 / 16X25X4
No. Final Filters / Size | 4 / 12X24X12
No. Final Filters / Size | 8 / 20X24X12
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | / 4@1800 |  | Horsepower / RPM | / 2@1200
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF |  |  | Rated Amperage / SF
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 15600 |  | Total CFM | 13600
Min OA CFM | 2400
Fan RPM | 2310 |  | Fan RPM | 1238
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage |  |  | RL Amperage
Motor B.H.P. | 67.74 |  | Motor B.H.P. | 8.414
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 8.018 |  | Total SP | 1.993
CW Coil P.D. | 0.893 |  |  |  |  | CHW COIL GPM | 92.38
[6 empty] | HW COIL GPM | NA
System Set Point
Pre Filters P.D.
Pre Filters P.D.
Total ESP | 4.0 |  | Total ESP | 1.1

## AHU-1-1 Valves
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX | [10 empty] | NOT FOUND ON DRAWING
DATA FROM SCHEDULE
Asset: AHU-1-1 Air Valves | [10 empty] | NO SUBMITTAL
Asset | Area Served | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max) | HW COIL GPM
SAV-1-1-01 | H.1302 | REHEAT | 6 | 150 |  | 100 |  | 130
SAV-1-1-02 | H.1301 | REHEAT | 6 | 600 |  | 410 |  | 410
SAV-1-1-03 | H.13C02A | REHEAT | 12 | 1800 |  | 330 |  | 1005
SAV-1-1-04 | H.1323 | REHEAT | 12 | 1950 |  | 1950 |  | 1950
SAV-1-1-05 | H.13C03 | REHEAT | 8 | 850 |  | 0 |  | 425
SAV-1-1-06 | H.1324 | REHEAT | 6 | 500 |  | 90 |  | 250
SAV-1-1-07 | H.13C03 | REHEAT | 6 | 300 |  | 180 |  | 180
SAV-1-1-08 | H.1311 | REHEAT | 14 | 2800 |  | 2800 |  | 2800
SAV-1-1-09 | H.1312 | REHEAT | 14 | 2800 |  | 2800 |  | 2800
SAV-1-1-10 | H.1309 | REHEAT | 14 | 2800 |  | 2800 |  | 2800
SAV-1-1-11 | H.1314 | REHEAT | 8 | 1050 |  | 225 |  | 252
RTU-1-1 SAV |  |  |  | 15600 | 0 |  |  | 13002 | 0
RAV-1-1-01 | H.1303 | RETURN | 6 | 250 |  | 50
RAV-1-1-02 | H.13C01 | RETURN | 12 | 2050 |  | 410
RAV-1-1-03 | H.1319 | RETURN | 10 | 1650 |  | 330
RAV-1-1-04 | H.1323 | RETURN | 10 | 1250 |  | 250
RAV-1-1-05 | H.13C03 | RETURN | 10 | 1150 |  | 230
RAV-1-1-06 | H.1324 | RETURN | 8 | 700 |  | 140
RAV-1-1-07 | H.13C03 | RETURN | 8 | 950 |  | 190
RAV-1-1-08 | H.1311 | RETURN | 12 | 2350 |  | 470
RAV-1-1-09 | H.1312 | RETURN | 12 | 2350 |  | 470
RAV-1-1-10 | H.1309 | RETURN | 12 | 2350 |  | 470
RAV-1-1-11 | H.1313 | RETURN | 10 | 1250 |  | 250
RTU-1-1 RAV |  |  |  | 16300 | 0
Note on C7: NTAB: BILLINGSLEY ONLY

## AHU-1-2
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: AHU-1-2 |  | Area: SURGERY |  |  |  | SUBMITTAL
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data |  |  | RETURN FAN | SECTION 3
Manufacturer | TRANE |  | Manufacturer |  |  | 4" ANGLE FILTER | SECTION 5
Model Number | CSAA050UA |  | Model Number |  |  | HW COIL | SECTION 6
Serial Number |  |  | Serial Number |  |  | CHW COIL | SECTION 10
Configuration | VERTICAL |  | Configuration | VERTICAL |  | SUPPLY FAN | SECTION 13
No. Pre Filters / Size | 36 / 20X20X4 |  | No. Pre Filters / Size |  |  | 12" BAG FILTER | SECTION 14
No. Pre Filters / Size | 5 / 12X24X4
No. Final Filters / Size | 5 / 12X24X12
No. Final Filters / Size | 10 / 24X24X12
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | / 4@1800 |  | Horsepower / RPM | / 4@1800
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF |  |  | Rated Amperage / SF
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 23000 |  | Total CFM | 13050
Min OA CFM | 9950
Fan RPM | 2863 |  | Fan RPM | 1790
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage |  |  | RL Amperage
Motor B.H.P. | 47.754 |  | Motor B.H.P. | 7.486
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 8.513 |  | Total SP | 2.203
CW Coil P.D. | 1.040 |  |  |  |  | CHW COIL GPM | 213.9
HW Coil P.D. | 0.023 |  |  |  |  | HW COIL GPM | 29.91
HW Coil P.D.
System Set Point
Pre Filters P.D.
Pre Filters P.D.
Total ESP | 4.20 |  | Total ESP | 1.0

## AHU-1-2 VAV's
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: AHU-1-2 VAV's | [10 empty] | SUBMITTAL
Asset | Area Served | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max) | HW COIL GPM
ATU-1-2-07 | H.1402 | HEAT | 8 | 500 |  | 500 |  | 500 |  |  | 2.61
ATU-1-2-08 | H.1402 | HEAT | 6 | 300 |  | 290 |  | 290 |  |  | 2.58
ATU-1-2-09 | H.1404 | HEAT | 14 | 2200 |  | 0 |  | 1100 |  |  | 6.06
ATU-1-2-10 | H.1405 | HEAT | 8 | 550 |  | 0 |  | 275 |  |  | 1.2
ATU-1-2-11 | H.15C03E | HEAT | 24X16 | 4350 |  | 870 |  | 2175 |  |  | 5.56
ATU-1-2-13 | H.15C03D | HEAT | 12 | 1450 |  | 0 |  | 725 |  |  | 2.23
RTU-1-2 VAV |  |  |  | 9350 | 0 |  |  | 5065 | 0
Note on C7: NTAB: BILLINGSLEY ONLY

## AHU-1-2 Valves
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX | [10 empty] | NOT FOUND ON DRAWING
DATA FROM SCHEDULE
Asset: AHU-1-2 Air Valves | [10 empty] | NO SUBMITTAL
Asset | Area Served | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max) | HW COIL GPM
SAV-1-2-01 | H.1325 | REHEAT | 12 | 2000 |  | 2000 |  | 2000
SAV-1-2-02 | H.13C03 | REHEAT | 8 | 850 |  | 0 |  | 425
SAV-1-2-03 | H.1319 | REHEAT | 14 | 2800 |  | 2800 |  | 2800
SAV-1-2-04 | H.1318 | REHEAT | 14 | 2800 |  | 2800 |  | 2800
SAV-1-2-05 | H.1315 | REHEAT | 14 | 2800 |  | 2800 |  | 2800
SAV-1-2-06 | H.13C04 | REHEAT | 10 | 1450 |  | 870 |  | 870
SAV-1-2-07 | H.1402 | REHEAT | 6 | 500 |  | 500 |  | 500
SAV-1-2-11 | [1] | REHEAT | 12 | 4350 |  | 870 |  | 2175
SAV-1-2-12 | H.1403 | REHEAT | 6 | 300 |  | 55 |  | 150
RTU-1-2 SAV |  |  |  | 17850 | 0 |  |  | 14520 | 0
RAV-1-2-01 | H.13C03 | RETURN | 10 | 1300 |  | 260
RAV-1-2-02 | H.13C03 | RETURN | 10 | 1150 |  | 230
RAV-1-2-03 | H.1319 | RETURN | 12 | 2350 |  | 470
RAV-1-2-04 | H.1318 | RETURN | 12 | 2350 |  | 470
RAV-1-2-05 | H.1315 | RETURN | 12 | 2350 |  | 470
RAV-1-2-06 | H.13C04 | RETURN | 10 | 1600 |  | 320
RAV-1-2-06A | H.1317 | RETURN | 6 | 350 |  | 70
RAV-1-2-07 | H.1401 | RETURN | 6 | 500 |  | 100
RAV-1-2-12 | H.1403 | RETURN | 6 | 300 |  | 60
RTU-1-2 RAV |  |  |  | 12250 | 0
EAV-1-2-11 | [1] | EXHAUST | 10 | 1650 |  | 330
RTU-1-2 EAV |  |  |  | 1650 | 0
NOTES: | [1] LISTED IN SCHEDULE, NOT MARKED ON DRAWING.
Note on C7: NTAB: BILLINGSLEY ONLY

## AHU-1-3
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: AHU-1-3 |  | Area: PREP & PACU |  |  |  | SUBMITTAL
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data |  |  | RETURN FAN | SECTION 2
Manufacturer | TRANE |  | Manufacturer | TRANE |  | 2" PRE-FILTER | SECTION 9
Model Number |  |  | Model Number |  |  | HW COIL | SECTION 10
Serial Number |  |  | Serial Number |  |  | CHW COIL | SECTION 12
Configuration | VERTICAL |  | Configuration | VERTICAL |  | SUPPLY FAN | SECTION 14
No. Pre Filters / Size | 20 / 24X24X2 |  | No. Pre Filters / Size |  |  | 12" BAG FILTER | SECTION 15
No. Pre Filters / Size | 4 / 12X24X2
No. Final Filters / Size | 20 / 24x24x12
No. Final Filters / Size | 4 / 12x24x12
EM2516T‐G |  |  | EHM3313T
Motor Data X |  |  | Motor Data X
Motor MFG / Frame | BALDOR / 256T |  | Motor MFG / Frame | BALDOR / 215T
Horsepower / RPM | 25 / 3515 |  | Horsepower / RPM | 10 / 1770
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 28 |  | Rated Amperage / SF | 12.5
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 36655 |  | Total CFM | 26550
Min OA CFM | 7450
Fan RPM | 3246 |  | Fan RPM | 1839
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage | 28 |  | RL Amperage | 12.5
Motor B.H.P. | 67.23 |  | Motor B.H.P. | 14.1
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 8.65 |  | Total SP | 2.12
CW Coil P.D. | 5.42 |  |  |  |  | CHW COIL GPM | 204.4
HW Coil P.D. | 0.09 |  |  |  |  | HW COIL GPM | 24
HW Coil P.D.
System Set Point
Pre Filters P.D.
Pre Filters P.D.
Total ESP | 4.9 |  | Total ESP

## AHU-1-3 VAV's (1)
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: AHU-1-3 VAV's | [10 empty] | SUBMITTAL
Asset | Area Served | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max) | HW COIL GPM
ATU-1-3-01 | H.1001 | HEAT | 8 | 500 |  | 500 |  | 500 |  |  | 1.9
ATU-1-3-02 | H.1102 | HEAT | 10 | 1000 |  | 480 |  | 690 |  |  | 2.9
ATU-1-3-03 | H.1207 | HEAT | 16 | 2000 |  | 0 |  | 1000 |  |  | 3.18
ATU-1-3-04 | H.1207 | HEAT | 12 | 1200 |  | 0 |  | 600 |  |  | 1.37
ATU-1-3-05 | H.11C03 | HEAT | 12 | 1300 |  | 780 |  | 780 |  |  | 2.11
ATU-1-3-06 | H.1107 | HEAT | 8 | 600 |  | 440 |  | 440 |  |  | 1.42
ATU-1-3-07 | H.1127 | HEAT | 8 | 700 |  | 515 |  | 515 |  |  | 2.05
ATU-1-3-08 | H.11C03 | HEAT | 12 | 1150 |  | 1150 |  | 1150 |  |  | 5.12
ATU-1-3-09 | H.1117 | HEAT | 6 | 250 |  | 90 |  | 125 |  |  | 0.25
ATU-1-3-10 | - | HEAT | 6 | 250 |  | 250 |  | 250 |  |  | 0.42
ATU-1-3-11 | - | HEAT | 8 | 700 |  | 700 |  | 700 |  |  | 1.94
ATU-1-3-12 | H.12C01 | HEAT | 10 | 750 |  | 750 |  | 750 |  |  | 3.59
ATU-1-3-13 | H.1204 | HEAT | 6 | 200 |  | 80 |  | 135 |  |  | 0.4
ATU-1-3-14 | H.1T01 | HEAT | 14 | 2000 |  | 0 |  | 1000 |  |  | 2.33
ATU-1-3-15 | H.1155A | HEAT | 8 | 405 |  | 405 |  | 405 |  |  | 1.2
ATU-1-3-16 | H.1129 | HEAT | 6 | 150 |  | 45 |  | 75 |  |  | 0.14
ATU-1-3-17 | H.1002 | HEAT | 8 | 650 |  | 640 |  | 640 |  |  | 4.3
ATU-1-3-18 | H.1005 | HEAT | 16 | 2300 |  | 425 |  | 1150 |  |  | 4.11
ATU-1-3-19 | H.1E01 | HEAT | 10 | 850 |  | 0 |  | 425 |  |  | 0.98
ATU-1-3-20 | H.1135 | HEAT | 8 | 650 |  | 110 |  | 325 |  |  | 0.81
ATU-1-3-21 | H.1152 | HEAT | 12 | 1550 |  | 930 |  | 930 |  |  | 2.98
ATU-1-3-22 | H.1130 | HEAT | 8 | 700 |  | 560 |  | 560 |  |  | 2.59
ATU-1-3-23 | H.1007A | HEAT | 10 | 1100 |  | 105 |  | 550 |  |  | 1.48
ATU-1-3-24 | H.1005 | HEAT | 16 | 2600 |  | 1400 |  | 1400 |  |  | 6.29
ATU-1-3-25 | H.1008 | HEAT | 8 | 400 |  | 160 |  | 200 |  |  | 0.4
ATU-1-3-26 | H.11C11 | HEAT | 10 | 1050 |  | 980 |  | 1025 |  |  | 3.85
ATU-1-3-27 | H.1159 | HEAT | 14 | 1700 |  | 1700 |  | 1700 |  |  | 6.77
ATU-1-3-28 | H.1162 | HEAT | 6 | 200 |  | 60 |  | 100 |  |  | 0.18
|  |  |  | 26905 | 0 |  |  | 18120 | 0
Note on C7: NTAB: BILLINGSLEY ONLY

## AHU-1-3 VAV's (2)
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: AHU-1-3 VAV's | [10 empty] | SUBMITTAL
Asset | Area Served | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max) | HW COIL GPM
ATU-1-3-30 | H.1151 | HEAT | 10 | 1000 |  | 700 |  | 700 |  |  | 2.4
ATU-1-3-31 | PHYS LOUNGE | HEAT | 8 | 700 |  | 210 |  | 350 |  |  | 0.92
ATU-1-3-32 | H.1335 | HEAT | 8 | 350 |  | 140 |  | 175 |  |  | 0.34
ATU-1-3-33 | H.1338 | HEAT | 8 | 450 |  | 105 |  | 105 |  |  | 0.47
ATU-1-3-34 | H.13C05 | HEAT | 8 | 700 |  | 190 |  | 350 |  |  | 0.92
ATU-1-3-35 | H.1341 | HEAT | 16 | 1850 |  | 0 |  | 925 |  |  | 1.86
ATU-1-3-36 | H.1343 | HEAT | 8 | 700 |  | 150 |  | 350 |  |  | 0.92
ATU-1-3-37 | H.1E02 | HEAT | 10 | 900 |  | 0 |  | 450 |  |  | 1.05
ATU-1-3-38 | H.1T02 | HEAT | 14 | 2000 |  | 0 |  | 1000 |  |  | 2.33
ATU-1-3-39 | H.1601 | HEAT | 6 | 150 |  | 45 |  | 75 |  |  | 0.14
ATU-1-3-40 | H.16C11 | HEAT | 8 | 650 |  | 650 |  | 65 |  |  | 6.95
ATU-1-3-41 | H.1602 | HEAT | 6 | 300 |  | 0 |  | 15 |  |  | 0.31
|  |  |  | 9750 | 0 |  |  | 4560 | 0
TOTAL |  |  |  | 36655 | 0 |  |  | 22680 | 0
Note on C7: NTAB: BILLINGSLEY ONLY

## AHU-1-3 Valves
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX | [10 empty] | NOT FOUND ON DRAWING
DATA FROM SCHEDULE
Asset: AHU-1-3 Air Valves | [10 empty] | NO SUBMITTAL
Asset | Area Served | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max) | HW COIL GPM
SAV-1-3-10 |  | REHEAT | 6 | 250 |  | 250 |  | 250
SAV-1-3-11 |  | REHEAT | 8 | 700 |  | 700 |  | 700
SAV-1-3-29 |  | REHEAT | 6 | 300 |  | 300 |  | 300
RTU-1-3 SAV |  |  |  | 1250 | 0 |  |  | 1250 | 0
EAV-1-3-10 |  | EXHAUST | 6 | 550 |  | 110
EAV-1-3-11 |  | EXHAUST | 8 | 1000 |  | 200
EAV-1-3-29 | [1] | EXHAUST | 6 | 600 |  | 120
RTU-1-3 EAV |  |  |  | 600 | 0
NOTES: | [1] LISTED IN SCHEDULE, NOT MARKED ON DRAWING.
Note on C7: NTAB: BILLINGSLEY ONLY

## AHU-1-4
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: AHU-1-4 |  | Area: ED & IMAGING |  |  |  | SUBMITTAL
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data |  |  | RETURN FAN | SECTION 2
Manufacturer | TRANE |  | Manufacturer | TRANE |  | 2" PRE-FILTER | SECTION 9
Model Number |  |  | Model Number |  |  | HW COIL | SECTION 10
Serial Number |  |  | Serial Number |  |  | CHW COIL | SECTION 12
Configuration | VERTICAL |  | Configuration | VERTICAL |  | SUPPLY FAN | SECTION 14
No. Pre Filters / Size | 24 / 24x24x2 |  | No. Pre Filters / Size |  |  | 12" BAG FILTER | SECTION 15
No. Pre Filters / Size | 10 / 12x24x2
No. Final Filters / Size | 24 / 24x24x12
No. Final Filters / Size | 10 / 12x24x12
EHM2535T |  |  | EHM2523T
Motor Data X |  |  | Motor Data X
Motor MFG / Frame | BALDOR / 286T |  | Motor MFG / Frame | BALDOR / 254T
Horsepower / RPM | 30 / 1775 |  | Horsepower / RPM | 15 / 1765
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 36 |  | Rated Amperage / SF | 18
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 47950 |  | Total CFM | 30350
Min OA CFM | 17650
Fan RPM | 2180 |  | Fan RPM | 2115
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage | 36 |  | RL Amperage | 18
Motor B.H.P. | 97.87 |  | Motor B.H.P. | 21.59
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 9.41 |  | Total SP | 2.89
CW Coil P.D. | 4.75 |  |  |  |  | CHW COIL GPM | 388.2
HW Coil P.D. | 0.53 |  |  |  |  | HW COIL GPM | 64.6
HW Coil P.D.
System Set Point
Pre Filters P.D.
Pre Filters P.D.
Total ESP | 5.3 |  | Total ESP

## AHU-1-4 VAV's (1)
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: AHU-1-4 VAV's | [10 empty] | SUBMITTAL
Asset | Area Served | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max) | HW COIL GPM
ATU-1-4-01 | H.1522 | HEAT | 8 | 500 |  | 95 |  | 250 |  |  | 0.62
ATU-1-4-02 | H.1515 | HEAT | 8 | 450 |  | 130 |  | 225 |  |  | 0.53
ATU-1-4-03 | H.1508 | HEAT | 8 | 300 |  | 120 |  | 150 |  |  | 0.31
ATU-1-4-04 | H.1022 | HEAT | 8 | 400 |  | 85 |  | 200 |  |  | 0.46
ATU-1-4-05 | H.1504 | HEAT | 8 | 600 |  | 170 |  | 300 |  |  | 0.85
ATU-1-4-06 | H.1503A | HEAT | 6 | 200 |  | 80 |  | 100 |  |  | 0.21
ATU-1-4-07 | H.1507 | HEAT | 8 | 500 |  | 80 |  | 250 |  |  | 0.62
ATU-1-4-08 | H.1022 | HEAT | 8 | 700 |  | 660 |  | 660 |  |  | 3.07
ATU-1-4-09 | H.1L02 | HEAT | 12 | 400 |  | 70 |  | 200 |  |  | 0.36
ATU-1-4-10 | H.1024 | HEAT | 10 | 800 |  | 240 |  | 400 |  |  | 1.03
ATU-1-4-11 | H.1S02 | HEAT | 10 | 950 |  | 950 |  | 950 |  |  | 4.18
ATU-1-4-12 | H.1605 | HEAT | 8 | 550 |  | 105 |  | 275 |  |  | 0.73
ATU-1-4-13 | H.1031 | HEAT | 8 | 700 |  | 140 |  | 350 |  |  | 2.16
ATU-1-4-14 | CHAPLIN | HEAT | 6 | 200 |  | 80 |  | 100 |  |  | 0.29
ATU-1-4-15 | H.1641 | HEAT | 14 | 2000 |  | 705 |  | 1000 |  |  | 2.75
ATU-1-4-16 | H.1632 | HEAT | 8 | 600 |  | 480 |  | 480 |  |  | 2.29
ATU-1-4-17 | H.16C03 | HEAT | 8 | 650 |  | 455 |  | 455 |  |  | 1.98
ATU-1-4-18 | H.1035 | HEAT | 12 | 1550 |  | 290 |  | 775 |  |  | 5.3
ATU-1-4-19 | H.1642 | HEAT | 8 | 350 |  | 105 |  | 175 |  |  | 0.38
ATU-1-4-20 | H.1T03 | HEAT | 14 | 1800 |  | 0 |  | 900 |  |  | 2.31
ATU-1-4-21 | H.16C07 | HEAT | 10 | 1000 |  | 600 |  | 600 |  |  | 2.18
ATU-1-4-22 | H.1623 | HEAT | 8 | 300 |  | 255 |  | 255 |  |  | 0.64
ATU-1-4-23 | H.1621 | HEAT | 10 | 950 |  | 950 |  | 950 |  |  | 4.18
ATU-1-4-24 | H.1614 | HEAT | 8 | 600 |  | 360 |  | 360 |  |  | 1.16
ATU-1-4-25 | H.1617 | HEAT | 10 | 750 |  | 430 |  | 430 |  |  | 1.16
ATU-1-4-26 | H.16C10 | HEAT | 10 | 1100 |  | 240 |  | 610 |  |  | 5.71
ATU-1-4-27 | H.1624 | HEAT | 8 | 500 |  | 270 |  | 270 |  |  | 0.72
ATU-1-4-28 | H.1628 | HEAT | 8 | 450 |  | 340 |  | 340 |  |  | 1.05
ATU-1-4-29 | H.1629 | HEAT | 6 | 250 |  | 105 |  | 125 |  |  | 0.27
|  |  |  | 20100 | 0 |  |  | 12135 | 0
Note on C7: NTAB: BILLINGSLEY ONLY

## AHU-1-4 VAV's (2)
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: AHU-1-4 VAV's | [10 empty] | SUBMITTAL
Asset | Area Served | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max) | HW COIL GPM
ATU-1-4-30 | H.1644 | HEAT | 10 | 800 |  | 800 |  | 800 |  |  | 4.96
ATU-1-4-31 | H.1709 | HEAT | 16 | 2850 |  | 2850 |  | 2850 |  |  | 6.97
ATU-1-4-32 | H.1703 | HEAT | 10 | 850 |  | 850 |  | 850 |  |  | 6.74
ATU-1-4-33 | H.1701A | HEAT | 8 | 450 |  | 450 |  | 450 |  |  | 7.24
ATU-1-4-34 | H.1716 | HEAT | 8 | 400 |  | 70 |  | 200 |  |  | 0.68
ATU-1-4-35 | H.1714A | HEAT | 8 | 400 |  | 160 |  | 200 |  |  | 0.46
ATU-1-4-36 | H.1711 | HEAT | 10 | 1050 |  | 280 |  | 525 |  |  | 1.64
ATU-1-4-37 | H.1E03 | HEAT | 12 | 1200 |  | 0 |  | 600 |  |  | 1.59
ATU-1-4-38 | H.1648 | HEAT | 8 | 300 |  | 70 |  | 150 |  |  | 0.31
ATU-1-4-39 | H.1649 | HEAT | 6 | 250 |  | 60 |  | 125 |  |  | 0.27
ATU-1-4-40 | H.1652 | HEAT | 12 | 1200 |  | 390 |  | 600 |  |  | 0.59
ATU-1-4-41 | H.1653 | HEAT | 8 | 300 |  | 65 |  | 150 |  |  | 0.31
ATU-1-4-42 | H.1654 | HEAT | 12 | 1200 |  | 380 |  | 600 |  |  | 1.59
ATU-1-4-43 | H.16C10 | HEAT | 10 | 1100 |  | 220 |  | 610 |  |  | 5.71
ATU-1-4-44 | H.16C09A | HEAT | 8 | 600 |  | 360 |  | 360 |  |  | 1.16
ATU-1-4-45 | H.1660 | HEAT | 8 | 450 |  | 300 |  | 300 |  |  | 0.85
ATU-1-4-46 | H.1659 | HEAT | 8 | 450 |  | 280 |  | 280 |  |  | 0.75
ATU-1-4-47 | H.1658 | HEAT | 8 | 400 |  | 290 |  | 290 |  |  | 0.79
ATU-1-4-48 | H.1655 | HEAT | 8 | 300 |  | 85 |  | 150 |  |  | 0.31
ATU-1-4-49 | H.17C01C | HEAT | 10 | 950 |  | 525 |  | 525 |  |  | 1.64
ATU-1-4-50 | H.1744 | HEAT | 8 | 450 |  | 390 |  | 390 |  |  | 1.38
ATU-1-4-51 | - | HEAT | 6 | 150 |  | 150 |  | 150 |  |  | 0.25
ATU-1-4-52 | H.1748 | HEAT | 8 | 300 |  | 260 |  | 260 |  |  | 0.66
ATU-1-4-53 | H.17C04 | HEAT | 12 | 1400 |  | 1400 |  | 1400 |  |  | 3.77
ATU-1-4-54 | H.1661 | HEAT | 6 | 250 |  | 30 |  | 125 |  |  | 0.4
ATU-1-4-55 | H.1752 | HEAT | 10 | 800 |  | 130 |  | 400 |  |  | 1.66
ATU-1-4-56 | H.1754 | HEAT | 8 | 400 |  | 400 |  | 400 |  |  | 1.46
ATU-1-4-57 | H.1757 | HEAT | 8 | 400 |  | 50 |  | 200 |  |  | 0.68
ATU-1-4-58 | H.1760 | HEAT | 10 | 1050 |  | 595 |  | 595 |  |  | 2.13
ATU-1-4-59 | H.1758 | HEAT | 6 | 200 |  | 200 |  | 200 |  |  | 0.55
|  |  |  | 20900 | 0 |  |  | 14735 | 0
Note on C7: NTAB: BILLINGSLEY ONLY

## AHU-1-4 VAV's (3)
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: AHU-1-4 VAV's | [10 empty] | SUBMITTAL
Asset | Area Served | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max) | HW COIL GPM
ATU-1-4-60 | H.1764 | HEAT | 6 | 250 |  | 100 |  | 125 |  |  | 0.27
ATU-1-4-61 | H.1737 | HEAT | 12 | 1300 |  | 1300 |  | 1300 |  |  | 4.57
ATU-1-4-62 | H.1736 | HEAT | 12 | 1300 |  | 1300 |  | 1300 |  |  | 4.57
ATU-1-4-63 | H.1735 | HEAT | 8 | 300 |  | 260 |  | 260 |  |  | 0.66
ATU-1-4-64 | H.17C04B | HEAT | 8 | 550 |  | 385 |  | 385 |  |  | 2.98
ATU-1-4-65 | H.1729 | HEAT | 8 | 350 |  | 90 |  | 210 |  |  | 0.73
ATU-1-4-66 | H.17C03 | HEAT | 8 | 550 |  | 250 |  | 450 |  |  | 1.92
ATU-1-4-67 | H.1725 | HEAT | 10 | 1000 |  | 0 |  | 500 |  |  | 2.79
ATU-1-4-68 | H.17C02 | HEAT | 10 | 900 |  | 780 |  | 780 |  |  | 5.43
ATU-1-4-69 | H.1718 | HEAT | 8 | 450 |  | 0 |  | 315 |  |  | 1.62
|  |  |  | 6950 | 0 |  |  | 5625 | 0
TOTAL |  |  |  | 47950 | 0 |  |  | 32495 | 0
Note on C7: NTAB: BILLINGSLEY ONLY

## AHU-1-4 Valves
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX | [10 empty] | NOT FOUND ON DRAWING
DATA FROM SCHEDULE
Asset: AHU-1-4 Air Valves | [10 empty] | NO SUBMITTAL
Asset | Area Served | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max) | HW COIL GPM
SAV-1-4-51 |  | REHEAT | 6 | 300 |  | 300 |  | 300
RTU-1-4 SAV |  |  |  | 300 | 0 |  |  | 300 | 0
EAV-1-4-51 |  | EXHAUST | 6 | 50 |  | 90
RTU-1-4 EAV |  |  |  | 50 | 0
NOTES: | [1] LISTED IN SCHEDULE, NOT MARKED ON DRAWING.
Note on C7: NTAB: BILLINGSLEY ONLY

## AHU-2-1
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: AHU-2-1 |  | Area: WOMEN'S SERVICES |  |  |  | SUBMITTAL
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data |  |  | RETURN FAN | SECTION 3
Manufacturer | TRANE |  | Manufacturer |  |  | 4" ANGLE FILTER | SECTION 5
Model Number | CSAA120UA |  | Model Number |  |  | HW COIL | NA
Serial Number |  |  | Serial Number |  |  | CHW COIL | SECTION 9
Configuration | VERTICAL |  | Configuration | VERTICAL |  | SUPPLY FAN | SECTION 12
No. Pre Filters / Size | 56 / 20X25X4 |  | No. Pre Filters / Size |  |  | 12" BAG FILTER | SECTION 13
No. Final Filters / Size | 7 / 12X24X12
No. Final Filters / Size | 4 / 24X12X12
No. Final Filters / Size | 28 / 24X24X12
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | / 4@1800 |  | Horsepower / RPM | / 4@1200
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF |  |  | Rated Amperage / SF
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 47950 |  | Total CFM | 43600
Min OA CFM | 17650
Fan RPM | 1782 |  | Fan RPM | 1554
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage |  |  | RL Amperage
Motor B.H.P. | 85.645 |  | Motor B.H.P. | 27.757
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 6.948 |  | Total SP | 2.336
CW Coil P.D. | 0.861 |  |  |  |  | CHW COIL GPM | 354.29
[6 empty] | HW COIL GPM | NA
System Set Point
Pre Filters P.D.
Pre Filters P.D.
Total ESP | 3.7 |  | Total ESP | 1.3

## AHU-2-1 VAV's (1)
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: AHU-2-1 VAV's | [10 empty] | SUBMITTAL
Asset | Area Served | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max) | HW COIL GPM
ATU-2-1-01 | H.2215 | HEAT | 8 | 650 |  | 610 |  | 610 |  |  | 5.71
ATU-2-1-02 | - | HEAT | 10 | 900 |  | 900 |  | 900 |  |  | 4.22
ATU-2-1-03 | H.2212 | HEAT | 8 | 450 |  | 370 |  | 370 |  |  | 2.57
ATU-2-1-04 | H.2211 | HEAT | 8 | 450 |  | 370 |  | 370 |  |  | 2.57
ATU-2-1-05 | H.2210 | HEAT | 8 | 450 |  | 370 |  | 370 |  |  | 2.57
ATU-2-1-06 | H.2209 | HEAT | 8 | 450 |  | 370 |  | 370 |  |  | 2.57
ATU-2-1-07 | H.2208 | HEAT | 8 | 450 |  | 370 |  | 370 |  |  | 2.57
ATU-2-1-08 | H.2207 | HEAT | 8 | 450 |  | 370 |  | 370 |  |  | 2.57
ATU-2-1-09 | H.2205 | HEAT | 8 | 450 |  | 370 |  | 370 |  |  | 2.57
ATU-2-1-10 | H.2204 | HEAT | 8 | 450 |  | 370 |  | 370 |  |  | 2.57
ATU-2-1-11 | H.2203 | HEAT | 8 | 450 |  | 340 |  | 340 |  |  | 1.98
ATU-2-1-12 | H.2229 | HEAT | 16 | 1800 |  | 1800 |  | 1800 |  |  | 7.38
ATU-2-1-15 | H.23C01A | HEAT | 8 | 700 |  | 700 |  | 700 |  |  | 3.76
ATU-2-1-17 | H.2311 | HEAT | 6 | 100 |  | 40 |  | 50 |  |  | 0.08
ATU-2-1-18 | H.23C02 | HEAT | 10 | 900 |  | 450 |  | 450 |  |  | 1.25
ATU-2-1-19 | H.2224 | HEAT | 6 | 150 |  | 60 |  | 75 |  |  | 0.14
ATU-2-1-20 | H.2304 | HEAT | 8 | 700 |  | 500 |  | 500 |  |  | 2.61
ATU-2-1-21 | H.22C02 | HEAT | 10 | 1000 |  | 630 |  | 830 |  |  | 3.48
ATU-2-1-22 | H.2217 | HEAT | 8 | 500 |  | 460 |  | 460 |  |  | 8.19
ATU-2-1-23 | H.2219 | HEAT | 6 | 200 |  | 35 |  | 100 |  |  | 0.29
ATU-2-1-24 | H.2E03 | HEAT | 8 | 550 |  | 0 |  | 275 |  |  | 1.2
ATU-2-1-25 | H.2415 | HEAT | 6 | 150 |  | 20 |  | 75 |  |  | 0.2
ATU-2-1-26 | H.2418 | HEAT | 8 | 300 |  | 220 |  | 265 |  |  | 1.11
ATU-2-1-27 | H.2412B | HEAT | 8 | 350 |  | 350 |  | 350 |  |  | 1.11
ATU-2-1-28 | - | HEAT | 8 | 300 |  | 300 |  | 300 |  |  | 0.55
ATU-2-1-29 | - | HEAT | 8 | 300 |  | 300 |  | 300 |  |  | 0.55
ATU-2-1-30 | H.2404 | HEAT | 12 | 1550 |  | 1395 |  | 1395 |  |  | 6.45
ATU-2-1-31 | H.2409 | HEAT | 12 | 1200 |  | 690 |  | 690 |  |  | 3.72
ATU-2-1-32 | H.2404A | HEAT | 6 | 200 |  | 80 |  | 105 |  |  | 0.31
ATU-2-1-33 | H.2405 | HEAT | 8 | 350 |  | 60 |  | 175 |  |  | 0.55
|  |  |  | 16900 | 0 |  |  | 13705 | 0
Note on C7: NTAB: BILLINGSLEY ONLY

## AHU-2-1 VAV's (2)
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: AHU-2-1 VAV's | [10 empty] | SUBMITTAL
Asset | Area Served | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max) | HW COIL GPM
ATU-2-1-34 | H.2402 | HEAT | 8 | 700 |  | 145 |  | 375 |  |  | 2.7
ATU-2-1-35 | H.2048 | HEAT | 8 | 550 |  | 110 |  | 275 |  |  | 0.73
ATU-2-1-36 | H.2050 | HEAT | 8 | 300 |  | 90 |  | 150 |  |  | 0.31
ATU-2-1-37 | H.2L01 | HEAT | 16 | 1850 |  | 1110 |  | 1110 |  |  | 2.82
ATU-2-1-38 | H.2T02 | HEAT | 16 | 2000 |  | 0 |  | 1000 |  |  | 2.4
ATU-2-1-39 | H.2043 | HEAT | 6 | 150 |  | 25 |  | 75 |  |  | 0.14
ATU-2-1-40 | H.2044 | HEAT | 6 | 150 |  | 25 |  | 75 |  |  | 0.14
ATU-2-1-41 | H.2042 | HEAT | 6 | 150 |  | 25 |  | 75 |  |  | 0.14
ATU-2-1-42 | H.2010 | HEAT | 8 | 350 |  | 260 |  | 260 |  |  | 0.66
ATU-2-1-43 |  | HEAT | 6 | 250 |  | 250 |  | 250 |  |  | 0.49
ATU-2-1-44 | H.2014 | HEAT | 10 | 750 |  | 570 |  | 570 |  |  | 4.26
ATU-2-1-45 | H.2009 | HEAT | 6 | 250 |  | 125 |  | 125 |  |  | 0.27
ATU-2-1-46 | H.2007 | HEAT | 10 | 750 |  | 220 |  | 375 |  |  | 1.48
ATU-2-1-47 | H.2003 | HEAT | 6 | 350 |  | 200 |  | 200 |  |  | 0.9
ATU-2-1-48 | H.2E02 | HEAT | 8 | 500 |  | 0 |  | 250 |  |  | 0.62
ATU-2-1-49 | H.20C02 | HEAT | 10 | 1000 |  | 1000 |  | 1000 |  |  | 4.91
ATU-2-1-50 | H.2001 | HEAT | 8 | 450 |  | 435 |  | 435 |  |  | 1.77
ATU-2-1-51 | H.2L02 | HEAT | 8 | 400 |  | 80 |  | 200 |  |  | 0.46
ATU-2-1-52 | H.2001 | HEAT | 16 | 2300 |  | 220 |  | 2100 |  |  | 6.26
ATU-2-1-53 | H.2101 | HEAT | 16 | 2100 |  | 2060 |  | 2060 |  |  | 6.56
ATU-2-1-54 | H.2102 | HEAT | 16 | 1900 |  | 1820 |  | 1820 |  |  | 6.4
ATU-2-1-55 | H.2102 | HEAT | 16 | 2100 |  | 2030 |  | 2030 |  |  | 5.92
ATU-2-1-56 | H.2102 | HEAT | 12 | 1500 |  | 1450 |  | 1450 |  |  | 7.13
ATU-2-1-57 | H.21C01 | HEAT | 8 | 700 |  | 400 |  | 400 |  |  | 1.46
ATU-2-1-59 | H.2M01 | HEAT | 16 | 2400 |  | 0 |  | 1200 |  |  | 5.41
ATU-2-1-60 | H.1020 | HEAT | 8 | 550 |  | 550 |  | 550 |  |  | 4.48
ATU-2-1-61 | H.1020B | HEAT | 6 | 150 |  | 20 |  | 75 |  |  | 0.2
ATU-2-1-62 | H.2002 | HEAT | 16 | 2000 |  | 395 |  | 1000 |  |  | 3.72
ATU-2-1-63 | HALLWAY | HEAT | 16 | 2700 |  | 605 |  | 1350 |  |  | 7.27
ATU-2-1-64 | H.2002 | HEAT | 14 | 1750 |  | 130 |  | 935 |  |  | 4.07
|  |  |  | 31050 | 0 |  |  | 21770 | 0
TOTAL |  |  |  | 47950 | 0 |  |  | 35475 | 0
Note on C7: NTAB: BILLINGSLEY ONLY

## AHU-2-1 Valves
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX | [10 empty] | NOT FOUND ON DRAWING
DATA FROM SCHEDULE
Asset: AHU-2-1 Air Valves | [10 empty] | NO SUBMITTAL
Asset | Area Served | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max) | HW COIL GPM
SAV-2-1-02 |  | REHEAT | 8 | 900 |  | 900 |  | 900
SAV-2-1-13 |  | REHEAT | 10 | 1400 |  | 1400 |  | 1400
SAV-2-1-14 |  | REHEAT | 10 | 1400 |  | 1400 |  | 1400
SAV-2-1-16 |  | REHEAT | 10 | 1400 |  | 1400 |  | 1400
SAV-2-1-28 |  | REHEAT | 6 | 300 |  | 300 |  | 300
SAV-2-1-29 |  | REHEAT | 6 | 300 |  | 300 |  | 300
SAV-2-1-43 |  | REHEAT | 6 | 250 |  | 250 |  | 250
RTU-2-1 SAV |  |  |  | 5950 | 0 |  |  | 5950 | 0
RAV-2-1-13 |  | RETURN | 8 | 1050 |  | 210
RAV-2-1-14 |  | RETURN | 8 | 1050 |  | 210
RAV-2-1-16 |  | RETURN | 8 | 1050 |  | 210
RTU-2-1 RAV |  |  |  | 3150 | 0
EAV-2-1-02 |  | EXHAUST | 10 | 1150 |  | 230
EAV-2-1-28 |  | EXHAUST | 6 | 600 |  | 120
EAV-2-1-29 |  | EXHAUST | 6 | 600 |  | 120
EAV-2-1-43 |  | EXHAUST | 6 | 550 |  | 110
RTU-2-1 EAV |  |  |  | 2900 | 0
Note on C7: NTAB: BILLINGSLEY ONLY

## AHU-3-1
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: AHU-3-1 |  | Area: ICU |  |  |  | SUBMITTAL
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data |  |  | RETURN FAN | SECTION 3
Manufacturer | TRANE |  | Manufacturer |  |  | 4" ANGLE FILTER | SECTION 5
Model Number | CSAA080UA |  | Model Number |  |  | HW COIL | SECTION 6
Serial Number |  |  | Serial Number |  |  | CHW COIL | SECTION 10
Configuration | VERTICAL |  | Configuration | VERTICAL |  | SUPPLY FAN | SECTION 13
No. Pre Filters / Size | 8 / 16X20X4 |  | No. Pre Filters / Size |  |  | 12" BAG FILTER | SECTION 14
No. Pre Filters / Size | 48 / 20X20X4
No. Final Filters / Size | 4 / 24X12X12
No. Final Filters / Size | 20 / 24X24X12
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | / 4@1800 |  | Horsepower / RPM | / 4@1200
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF |  |  | Rated Amperage / SF
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 34950 |  | Total CFM | 25300
Min OA CFM | 9700
Fan RPM | 2282 |  | Fan RPM | 1440
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage |  |  | RL Amperage
Motor B.H.P. | 64.935 |  | Motor B.H.P. | 13.185
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 8.29 |  | Total SP | 1.989
CW Coil P.D. | 0.796 |  |  |  |  | CHW COIL GPM | 223.63
HW Coil P.D. | 0.055 |  |  |  |  | HW COIL GPM | 40.59
HW Coil P.D.
System Set Point
Pre Filters P.D.
Pre Filters P.D.
Total ESP | 4.3 |  | Total ESP | 1.10

## AHU-3-1 VAV's (1)
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: AHU-3-1 VAV's | [10 empty] | SUBMITTAL
Asset | Area Served | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max) | HW COIL GPM
ATU-3-1-01 | H.3410 | HEAT | 6 | 400 |  | 310 |  | 310 |  |  | 2.24
ATU-3-1-02 | H.3409 | HEAT | 8 | 300 |  | 290 |  | 290 |  |  | 1.11
ATU-3-1-03 | H.3408 | HEAT | 8 | 300 |  | 290 |  | 290 |  |  | 1.11
ATU-3-1-04 | H.3407 | HEAT | 8 | 300 |  | 290 |  | 290 |  |  | 1.11
ATU-3-1-05 | H.3405 | HEAT | 8 | 300 |  | 290 |  | 290 |  |  | 1.11
ATU-3-1-06 | H.3404 | HEAT | 8 | 300 |  | 290 |  | 290 |  |  | 1.11
ATU-3-1-07 | H.3403 | HEAT | 8 | 300 |  | 290 |  | 290 |  |  | 1.11
ATU-3-1-08 | - | HEAT | 10 | 750 |  | 750 |  | 750 |  |  | 2.85
ATU-3-1-09 | H.3303 | HEAT | 8 | 600 |  | 125 |  | 300 |  |  | 1.18
ATU-3-1-10 | H.3302 | HEAT | 6 | 400 |  | 215 |  | 215 |  |  | 0.86
ATU-3-1-11 | H.3424 | HEAT | 12 | 1150 |  | 115 |  | 575 |  |  | 2.03
ATU-3-1-12 | H.3421 | HEAT | 8 | 350 |  | 300 |  | 300 |  |  | 1.18
ATU-3-1-13 | H.3420 | HEAT | 8 | 350 |  | 280 |  | 280 |  |  | 1.03
ATU-3-1-14 | H.3419 | HEAT | 8 | 350 |  | 280 |  | 280 |  |  | 1.03
ATU-3-1-15 | H.3418 | HEAT | 8 | 350 |  | 280 |  | 280 |  |  | 1.03
ATU-3-1-16 | H.3417 | HEAT | 8 | 350 |  | 280 |  | 280 |  |  | 1.03
ATU-3-1-17 | H.3415 | HEAT | 8 | 350 |  | 280 |  | 280 |  |  | 1.03
ATU-3-1-18 | H.3414 | HEAT | 8 | 350 |  | 290 |  | 290 |  |  | 1.11
ATU-3-1-19 | H.3413 | HEAT | 8 | 350 |  | 290 |  | 290 |  |  | 1.11
ATU-3-1-20 | H.3412 | HEAT | 8 | 350 |  | 290 |  | 290 |  |  | 1.11
ATU-3-1-21 | H.3411 | HEAT | 8 | 350 |  | 310 |  | 310 |  |  | 1.27
ATU-3-1-22 | H.34C03A | HEAT | 14 | 1650 |  | 1075 |  | 1545 |  |  | 5.31
ATU-3-1-23 | H.34C04 | HEAT | 12 | 1250 |  | 1250 |  | 1250 |  |  | 3.85
ATU-3-1-24 | H.3437 | HEAT | 8 | 700 |  | 135 |  | 350 |  |  | 0.92
ATU-3-1-25 | H.3E03 | HEAT | 8 | 300 |  | 0 |  | 150 |  |  | 0.27
ATU-3-1-26 | H.3435 | HEAT | 6 | 200 |  | 60 |  | 100 |  |  | 0.18
ATU-3-1-27 | H.3432 | HEAT | 6 | 200 |  | 60 |  | 100 |  |  | 0.18
ATU-3-1-28 | H.3431A | HEAT | 6 | 200 |  | 55 |  | 100 |  |  | 0.18
ATU-3-1-29 | H.3428 | HEAT | 8 | 350 |  | 175 |  | 175 |  |  | 0.34
|  |  |  | 13450 | 0 |  |  | 10540 | 0
Note on C7: NTAB: BILLINGSLEY ONLY

## AHU-3-1 VAV's (2)
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: AHU-3-1 VAV's | [10 empty] | SUBMITTAL
Asset | Area Served | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max) | HW COIL GPM
ATU-3-1-30 | H.32C02 | HEAT | 8 | 600 |  | 390 |  | 390 |  |  | 1.11
ATU-3-1-31 | H.3425 | HEAT | 8 | 500 |  | 105 |  | 250 |  |  | 0.55
ATU-3-1-32 | H.3T02 | HEAT | 16 | 2050 |  | 0 |  | 1025 |  |  | 2.15
ATU-3-1-33 | H.3M01 | HEAT | 14 | 1750 |  | 0 |  | 875 |  |  | 2.99
ATU-3-1-34 | H.3005 | HEAT | 10 | 850 |  | 225 |  | 425 |  |  | 0.98
ATU-3-1-35 | H.32C01B | HEAT | 10 | 1000 |  | 1000 |  | 1000 |  |  | 4.43
ATU-3-1-36 | H.3202 | HEAT | 8 | 550 |  | 45 |  | 275 |  |  | 0.62
ATU-3-1-37 | - | HEAT | 6 | 100 |  | 100 |  | 100 |  |  | 0.14
ATU-3-1-38 | H.3209 | HEAT | 8 | 300 |  | 270 |  | 270 |  |  | 0.6
ATU-3-1-39 | H.3L02 | HEAT | 8 | 400 |  | 80 |  | 200 |  |  | 0.4
ATU-3-1-40 | H.3001 | HEAT | 10 | 1000 |  | 180 |  | 500 |  |  | 2.2
ATU-3-1-41 | H.30C01 | HEAT | 8 | 450 |  | 270 |  | 270 |  |  | 0.6
ATU-3-1-42 | H.3135 | HEAT | 6 | 200 |  | 80 |  | 100 |  |  | 0.18
ATU-3-1-43 | H.3122 | HEAT | 8 | 400 |  | 250 |  | 250 |  |  | 0.85
ATU-3-1-44 | H.3121 | HEAT | 8 | 400 |  | 280 |  | 280 |  |  | 1.03
ATU-3-1-45 | H.3120 | HEAT | 8 | 400 |  | 280 |  | 280 |  |  | 1.03
ATU-3-1-46 | H.3119 | HEAT | 8 | 400 |  | 280 |  | 280 |  |  | 1.03
ATU-3-1-47 | H.3118 | HEAT | 8 | 400 |  | 280 |  | 280 |  |  | 1.03
ATU-3-1-48 | H.3117 | HEAT | 8 | 400 |  | 250 |  | 250 |  |  | 0.85
ATU-3-1-49 | - | HEAT | 10 | 1000 |  | 1000 |  | 1000 |  |  | 4.43
ATU-3-1-50 | H.3113 | HEAT | 8 | 300 |  | 240 |  | 240 |  |  | 0.79
ATU-3-1-51 | H.3112 | HEAT | 8 | 300 |  | 270 |  | 270 |  |  | 0.98
ATU-3-1-52 | H.3111 | HEAT | 8 | 350 |  | 40 |  | 175 |  |  | 0.47
ATU-3-1-53 | H.3110 | HEAT | 8 | 350 |  | 350 |  | 350 |  |  | 1.66
ATU-3-1-54 | H.3109 | HEAT | 8 | 350 |  | 280 |  | 280 |  |  | 1.03
ATU-3-1-55 | H.3108 | HEAT | 8 | 350 |  | 280 |  | 280 |  |  | 1.03
ATU-3-1-56 | H.3107 | HEAT | 8 | 350 |  | 280 |  | 280 |  |  | 1.03
ATU-3-1-57 | H.3105 | HEAT | 8 | 350 |  | 280 |  | 280 |  |  | 1.03
ATU-3-1-58 | H.3104 | HEAT | 8 | 350 |  | 280 |  | 280 |  |  | 1.03
ATU-3-1-59 | H.3103 | HEAT | 8 | 350 |  | 280 |  | 280 |  |  | 0.85
|  |  |  | 16550 | 0 |  |  | 11015 | 0
Note on C7: NTAB: BILLINGSLEY ONLY

## AHU-3-1 VAV's (3)
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: AHU-3-1 VAV's | [10 empty] | SUBMITTAL
Asset | Area Served | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max) | HW COIL GPM
ATU-3-1-60 | H.3102 | HEAT | 8 | 450 |  | 250 |  | 250 |  |  | 0.85
ATU-3-1-61 | H.3101 | HEAT | 8 | 450 |  | 270 |  | 270 |  |  | 0.98
ATU-3-1-62 | H.31C01 | HEAT | 10 | 1050 |  | 1050 |  | 1050 |  |  | 4.11
ATU-3-1-63 | H.31C02 | HEAT | 12 | 1300 |  | 845 |  | 845 |  |  | 2.44
ATU-3-1-64 | H.3134 | HEAT | 8 | 350 |  | 95 |  | 175 |  |  | 0.34
ATU-3-1-65 | H.3E02 | HEAT | 8 | 350 |  | 0 |  | 175 |  |  | 0.34
ATU-3-1-66 | H.3129 | HEAT | 6 | 200 |  | 60 |  | 100 |  |  | 0.18
ATU-3-1-67 | H.3127 | HEAT | 8 | 300 |  | 90 |  | 150 |  |  | 0.27
ATU-3-1-68 | H.3125 | HEAT | 8 | 500 |  | 30 |  | 250 |  |  | 0.55
|  |  |  | 4950 | 0 |  |  | 3265 | 0
TOTAL |  |  |  | 34950 | 0 |  |  | 24820 | 0
Note on C7: NTAB: BILLINGSLEY ONLY

## AHU-3-1 Valves
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX | [10 empty] | NOT FOUND ON DRAWING
DATA FROM SCHEDULE
Asset: AHU-3-1 Air Valves | [10 empty] | NO SUBMITTAL
Asset | Area Served | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max) | HW COIL GPM
SAV-3-1-08 |  | REHEAT | 8 | 750 |  | 750 |  | 750
SAV-3-1-37 |  | REHEAT | 6 | 100 |  | 100 |  | 100
SAV-3-1-49 |  | REHEAT | 8 | 1000 |  | 1000 |  | 1000
RTU-3-1 SAV |  |  |  | 1850 | 0 |  |  | 1850 | 0
EAV-3-1-08 |  | EXHAUST | 8 | 1050 |  | 210
EAV-3-1-37 |  | EXHAUST | 6 | 400 |  | 80
EAV-3-1-49 |  | EXHAUST | 10 | 1300 |  | 260
RTU-3-1 EAV |  |  |  | 2750 | 0
NOTES: | [1] LISTED IN SCHEDULE, NOT MARKED ON DRAWING.
Note on C7: NTAB: BILLINGSLEY ONLY

## AHU-4-1
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: AHU-4-1 |  | Area: LVL 4 MED-SURG |  |  |  | SUBMITTAL
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data |  |  | RETURN FAN | SECTION 3
Manufacturer | TRANE |  | Manufacturer |  |  | 4" ANGLE FILTER | SECTION 5
Model Number | CSAA080UA |  | Model Number |  |  | HW COIL | SECTION 6
Serial Number |  |  | Serial Number |  |  | CHW COIL | SECTION 10
Configuration | VERTICAL |  | Configuration | VERTICAL |  | SUPPLY FAN | SECTION 13
No. Pre Filters / Size | 8 / 16X20X4 |  | No. Pre Filters / Size |  |  | 12" BAG FILTER | SECTION 14
No. Pre Filters / Size | 48 / 20X20X4
No. Final Filters / Size | 4 / 24X12X12
No. Final Filters / Size | 20 / 24X24X12
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | / 4@1800 |  | Horsepower / RPM | / 4@1800
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF |  |  | Rated Amperage / SF
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 37000 |  | Total CFM | 28250
Min OA CFM | 8750
Fan RPM | 2306 |  | Fan RPM | 1819
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage |  |  | RL Amperage
Motor B.H.P. | 67.426 |  | Motor B.H.P. | 20.733
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 8.116 |  | Total SP | 2.464
CW Coil P.D. | 0.871 |  |  |  |  | CHW COIL GPM | 226
HW Coil P.D. | 0.015 |  |  |  |  | HW COIL GPM | 38.03
HW Coil P.D.
System Set Point
Pre Filters P.D.
Pre Filters P.D.
Total ESP | 4.0 |  | Total ESP | 1.5

## AHU-4-1 VAV's (1)
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: AHU-4-1 VAV's | [10 empty] | SUBMITTAL
Asset | Area Served | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max) | HW COIL GPM
ATU-4-1-01 | H.4210 | HEAT | 8 | 550 |  | 250 |  | 300 |  |  | 1.11
ATU-4-1-02 | H.4209 | HEAT | 8 | 500 |  | 280 |  | 280 |  |  | 0.98
ATU-4-1-03 | H.4208 | HEAT | 8 | 500 |  | 280 |  | 280 |  |  | 0.98
ATU-4-1-04 | H.4207 | HEAT | 8 | 500 |  | 250 |  | 250 |  |  | 0.81
ATU-4-1-05 | H.4E02 | HEAT | 12 | 1500 |  | 20 |  | 750 |  |  | 3.33
ATU-4-1-06 | H4204 | HEAT | 8 | 500 |  | 280 |  | 280 |  |  | 0.98
ATU-4-1-07 | H.4203 | HEAT | 8 | 500 |  | 280 |  | 280 |  |  | 0.98
ATU-4-1-08 | H.4202 | HEAT | 8 | 500 |  | 280 |  | 280 |  |  | 0.98
ATU-4-1-09 | H.4201 | HEAT | 8 | 500 |  | 280 |  | 280 |  |  | 0.98
ATU-4-1-10 | H.4020 | HEAT | 8 | 300 |  | 0 |  | 150 |  |  | 0.27
ATU-4-1-11 | H.4222 | HEAT | 8 | 500 |  | 280 |  | 280 |  |  | 0.98
ATU-4-1-12 | H.4221 | HEAT | 8 | 500 |  | 280 |  | 280 |  |  | 0.98
ATU-4-1-13 | H.4220 | HEAT | 8 | 500 |  | 280 |  | 280 |  |  | 0.98
ATU-4-1-14 | H.4219 | HEAT | 8 | 500 |  | 280 |  | 280 |  |  | 0.98
ATU-4-1-15 | H.4218 | HEAT | 8 | 500 |  | 270 |  | 270 |  |  | 0.92
ATU-4-1-16 | H.4217 | HEAT | 8 | 550 |  | 90 |  | 275 |  |  | 0.94
ATU-4-1-17 | H.4214 | HEAT | 8 | 500 |  | 250 |  | 250 |  |  | 0.81
ATU-4-1-18 | H.4213 | HEAT | 8 | 500 |  | 280 |  | 280 |  |  | 0.98
ATU-4-1-19 | H.4212 | HEAT | 8 | 500 |  | 280 |  | 280 |  |  | 0.98
ATU-4-1-20 | H.4211 | HEAT | 8 | 500 |  | 230 |  | 250 |  |  | 0.81
ATU-4-1-21 | H.40C02 | HEAT | 10 | 1000 |  | 1000 |  | 1000 |  |  | 3.22
ATU-4-1-22 | H.4019 | HEAT | 8 | 750 |  | 40 |  | 375 |  |  | 1.83
ATU-4-1-23 | H.4018 | HEAT | 6 | 200 |  | 90 |  | 135 |  |  | 0.38
ATU-4-1-24 | H.4M01 | HEAT | 16 | 1800 |  | 310 |  | 900 |  |  | 2.54
ATU-4-1-25 | H.4L01 | HEAT | 8 | 400 |  | 30 |  | 200 |  |  | 0.38
ATU-4-1-26 | H.4021 | [10 empty] | MISSING FROM SUBMITTAL
ATU-4-1-27 | H.4013 | HEAT | 8 | 400 |  | 115 |  | 200 |  |  | 0.38
ATU-4-1-28 | - | HEAT | 10 | 950 |  | 950 |  | 950 |  |  | 2.91
ATU-4-1-29 | H.4014 | HEAT | 12 | 1300 |  | 715 |  | 715 |  |  | 1.7
|  |  |  | 17700 | 0 |  |  | 10330 | 0
Note on C7: NTAB: BILLINGSLEY ONLY

## AHU-4-1 VAV's (2)
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: AHU-4-1 VAV's | [10 empty] | SUBMITTAL
Asset | Area Served | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max) | HW COIL GPM
ATU-4-1-30 | H.4L02 | HEAT | 8 | 400 |  | 80 |  | 200 |  |  | 0.38
ATU-4-1-31 | H.4001 | HEAT | 10 | 850 |  | 185 |  | 700 |  |  | 2.79
ATU-4-1-32 | H.4009 | HEAT | 6 | 200 |  | 60 |  | 100 |  |  | 0.25
ATU-4-1-33 | H.4101 | HEAT | 8 | 450 |  | 270 |  | 270 |  |  | 0.92
ATU-4-1-34 | H.4102 | HEAT | 8 | 400 |  | 250 |  | 250 |  |  | 0.81
ATU-4-1-35 | H.4E01 | HEAT | 12 | 1500 |  | 20 |  | 750 |  |  | 3.33
ATU-4-1-36 | H.4008 | HEAT | 8 | 450 |  | 120 |  | 225 |  |  | 0.68
ATU-4-1-37 | H.4011 | HEAT | 12 | 1200 |  | 135 |  | 600 |  |  | 2.07
ATU-4-1-38 | H.4010 | HEAT | 8 | 650 |  | 40 |  | 325 |  |  | 0.75
ATU-4-1-39 | H.4009 | HEAT | 10 | 1000 |  | 645 |  | 645 |  |  | 1.87
ATU-4-1-40 | H.4124 | HEAT | 8 | 550 |  | 250 |  | 275 |  |  | 0.94
ATU-4-1-41 | H.4123 | HEAT | 8 | 550 |  | 280 |  | 280 |  |  | 0.98
ATU-4-1-42 | H.4122 | HEAT | 8 | 550 |  | 280 |  | 280 |  |  | 0.98
ATU-4-1-43 | H.4121 | HEAT | 8 | 550 |  | 270 |  | 275 |  |  | 0.94
ATU-4-1-44 | H.4119 | HEAT | 8 | 500 |  | 70 |  | 250 |  |  | 0.81
ATU-4-1-45 | H.4118 | HEAT | 8 | 550 |  | 280 |  | 280 |  |  | 0.98
ATU-4-1-46 | H.4117 | HEAT | 8 | 550 |  | 280 |  | 280 |  |  | 0.98
ATU-4-1-47 | H.4115 | HEAT | 8 | 550 |  | 250 |  | 275 |  |  | 0.94
ATU-4-1-48 | - | HEAT | 10 | 1000 |  | 1000 |  | 1000 |  |  | 4.09
ATU-4-1-49 | H.4112 | HEAT | 8 | 350 |  | 350 |  | 350 |  |  | 0.86
ATU-4-1-50 | H.4111 | HEAT | 8 | 450 |  | 250 |  | 250 |  |  | 0.81
ATU-4-1-51 | H.4110 | HEAT | 8 | 450 |  | 280 |  | 280 |  |  | 0.98
ATU-4-1-52 | H.4109 | HEAT | 8 | 450 |  | 280 |  | 280 |  |  | 0.098
ATU-4-1-53 | H.4108 | HEAT | 8 | 450 |  | 280 |  | 280 |  |  | 0.98
ATU-4-1-54 | H.4107 | HEAT | 8 | 450 |  | 280 |  | 280 |  |  | 0.98
ATU-4-1-55 | H.4105 | HEAT | 8 | 450 |  | 280 |  | 280 |  |  | 0.98
ATU-4-1-56 | H.4104 | HEAT | 8 | 450 |  | 280 |  | 280 |  |  | 0.98
ATU-4-1-57 | H.4103 | HEAT | 8 | 450 |  | 250 |  | 250 |  |  | 0.81
ATU-4-1-58 | H.40C01 | HEAT | 10 | 850 |  | 625 |  | 625 |  |  | 1.75
|  |  |  | 17250 | 0 |  |  | 10415 | 0
TOTAL |  |  |  | 34950 | 0 |  |  | 20745 | 0
Note on C7: NTAB: BILLINGSLEY ONLY

## AHU-4-1 Valves
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX | [10 empty] | NOT FOUND ON DRAWING
DATA FROM SCHEDULE
Asset: AHU-4-1 Air Valves | [10 empty] | NO SUBMITTAL
Asset | Area Served | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max) | HW COIL GPM
SAV-4-1-28 |  | REHEAT | 8 | 950 |  | 950 |  | 950
SAV-4-1-48 |  | REHEAT | 8 | 1000 |  | 1000 |  | 1000
RTU-4-1 SAV |  |  |  | 1950 | 0 |  |  | 1950 | 0
EAV-4-1-28 |  | EXHAUST | 10 | 1250 |  | 250
EAV-4-1-48 |  | EXHAUST | 10 | 1300 |  | 260
RTU-4-1 EAV |  |  |  | 2550 | 0
NOTES: | [1] LISTED IN SCHEDULE, NOT MARKED ON DRAWING.
Note on C7: NTAB: BILLINGSLEY ONLY

## FCU-CEP-1A
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: FCU-CEP-1A |  | Area: CHILLER ROOM
Unit Data |  |  |  |  | Test Data
MFG | TRANE |  |  |  |  | Design | Actual
Model Num | UCCAD10 |  |  |  | SA CFM | 4500 |  | CHW COIL GPM | 47.94
Serial Num |  |  |  |  | Fan Speed | 1225 |  | HW COIL GPM | 35.49
OA CFM
RA CFM
Motor Data |  |  |  |  | RL Voltage | 460
Motor MFG |  |  |  |  | RL Amperage | 8.42
Horsepower | 5 |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase | 3 |  |  |  | Total ESP | 1
Voltage (rated) | 460 |  |  |  | Brake HP | 3.613
Amperage (rated) | 8.42
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU-CEP-1B
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: FCU-CEP-1B |  | Area: CHILLER ROOM
Unit Data |  |  |  |  | Test Data
MFG | TRANE |  |  |  |  | Design | Actual
Model Num | UCCAD10 |  |  |  | SA CFM | 4500 |  | CHW COIL GPM | 47.94
Serial Num |  |  |  |  | Fan Speed | 1225 |  | HW COIL GPM | 35.49
OA CFM
RA CFM
Motor Data |  |  |  |  | RL Voltage | 460
Motor MFG |  |  |  |  | RL Amperage | 8.42
Horsepower | 5 |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase | 3 |  |  |  | Total ESP | 1
Voltage (rated) | 460 |  |  |  | Brake HP | 3.613
Amperage (rated) | 8.42
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU-CEP-2
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: FCU-CEP-2 |  | Area: PLUMBING ROOM
Unit Data |  |  |  |  | Test Data
MFG | TRANE |  |  |  |  | Design | Actual
Model Num | BCVE072G |  |  |  | SA CFM | 2000 |  | CHW COIL GPM | 7.7
Serial Num |  |  |  |  | Fan Speed | 1635 |  | HW COIL GPM | 1.03
OA CFM
RA CFM
Motor Data |  |  |  |  | RL Voltage | 460
Motor MFG |  |  |  |  | RL Amperage | 3.3
Horsepower | 1.5 |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase | 3 |  |  |  | Total ESP | 1
Voltage (rated) | 460 |  |  |  | Brake HP | 1.392
Amperage (rated) | 3.3
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU-CEP-3
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: FCU-CEP-3 |  | Area: MED GAS EQUIP ROOM
Unit Data |  |  |  |  | Test Data
MFG | TRANE |  |  |  |  | Design | Actual
Model Num | BCVE090G |  |  |  | SA CFM | 3000 |  | CHW COIL GPM | 5.61
Serial Num |  |  |  |  | Fan Speed | 1233 |  | HW COIL GPM | 1.71
OA CFM
RA CFM
Motor Data |  |  |  |  | RL Voltage | 460
Motor MFG |  |  |  |  | RL Amperage | 5.5
Horsepower | 3 |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase | 3 |  |  |  | Total ESP | 1
Voltage (rated) | 460 |  |  |  | Brake HP | 1.819
Amperage (rated) | 5.5
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU-CEP-4
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: FCU-CEP-4 |  | Area: BOILER ROOM
Unit Data |  |  |  |  | Test Data
MFG | TRANE |  |  |  |  | Design | Actual
Model Num | BCVE090G |  |  |  | SA CFM | 3000 |  | CHW COIL GPM | 11.86
Serial Num |  |  |  |  | Fan Speed | 1266 |  | HW COIL GPM | 1.71
OA CFM
RA CFM
Motor Data |  |  |  |  | RL Voltage | 460
Motor MFG |  |  |  |  | RL Amperage | 5.5
Horsepower | 3 |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase | 3 |  |  |  | Total ESP | 1
Voltage (rated) | 460 |  |  |  | Brake HP | 1.891
Amperage (rated) | 5.5
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU-CEP-5
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: FCU-CEP-5 |  | Area: MED GAS MANIFOLD ROOM
Unit Data |  |  |  |  | Test Data
MFG | TRANE |  |  |  |  | Design | Actual
Model Num | BCVE018G |  |  |  | SA CFM | 400 |  | CHW COIL GPM | 1.32
Serial Num |  |  |  |  | Fan Speed | 1500 |  | HW COIL GPM | 0.62
OA CFM
RA CFM
Motor Data |  |  |  |  | RL Voltage | 460
Motor MFG |  |  |  |  | RL Amperage | 1.3
Horsepower | 0.5 |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase | 3 |  |  |  | Total ESP | 1
Voltage (rated) | 460 |  |  |  | Brake HP | 0.198
Amperage (rated) | 1.3
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU-CEP-6
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: FCU-CEP-6 |  | Area: FIRE PUMP ROOM
Unit Data |  |  |  |  | Test Data
MFG | TRANE |  |  |  |  | Design | Actual
Model Num | BCVE072G |  |  |  | SA CFM | 2000 |  | CHW COIL GPM | 7.24
Serial Num |  |  |  |  | Fan Speed | 1630 |  | HW COIL GPM | 1.03
OA CFM
RA CFM
Motor Data |  |  |  |  | RL Voltage | 460
Motor MFG |  |  |  |  | RL Amperage | 3.3
Horsepower | 1.5 |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase | 3 |  |  |  | Total ESP | 1
Voltage (rated) | 460 |  |  |  | Brake HP | 1.386
Amperage (rated) | 3.3
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU-CEP-7
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: FCU-CEP-7 |  | Area: MAIN ELECTRICAL ROOM
Unit Data |  |  |  |  | Test Data
MFG | TRANE |  |  |  |  | Design | Actual
Model Num | BCVE090G |  |  |  | SA CFM | 3000 |  | CHW COIL GPM | 9.54
Serial Num |  |  |  |  | Fan Speed | 1179 |  | HW COIL GPM | 1.71
OA CFM
RA CFM
Motor Data |  |  |  |  | RL Voltage | 460
Motor MFG |  |  |  |  | RL Amperage | 5.5
Horsepower | 3 |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase | 3 |  |  |  | Total ESP | 1
Voltage (rated) | 460 |  |  |  | Brake HP | 1.733
Amperage (rated) | 5.5
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU-CEP-8
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: FCU-CEP-8 |  | Area: EMERGENCY ELECT ROOM
Unit Data |  |  |  |  | Test Data
MFG | TRANE |  |  |  |  | Design | Actual
Model Num | BCVE090G |  |  |  | SA CFM | 3600 |  | CHW COIL GPM | 7.5
Serial Num |  |  |  |  | Fan Speed | 1282 |  | HW COIL GPM | 2.02
OA CFM
RA CFM
Motor Data |  |  |  |  | RL Voltage | 460
Motor MFG |  |  |  |  | RL Amperage | 5.5
Horsepower | 3 |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase | 3 |  |  |  | Total ESP | 1
Voltage (rated) | 460 |  |  |  | Brake HP | 2.55
Amperage (rated) | 5.5
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## KEF-1
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: KEF-1 |  |  | Serves: KITCHEN HOOD 1 |  |  |  |  | SUBMITTAL
Unit Data |  |  |  |  | Drive Data
MFG |  | GREENHECK |  |  | Motor Sheave Size
Model Num |  | USF-18 |  |  | Motor Bore Size
Serial Num |  |  |  |  | Fan Sheave Size
Type |  | BELTED VENT FAN |  |  | Fan Bore Size
Belt CL Distance
Motor Data |  |  |  |  | No of Belts
Motor MFG |  |  |  |  | Belt Size
Frame |  | 182T
Horsepower |  | 3 |  |  | Test Data
Motor Rpm |  | 1725 |  |  |  | Design | Actual
Phase |  | 3 |  |  | CFM | 3600
Voltage (rated) |  | 460 |  |  | Fan RPM | 1454
Amperage (rated) |  | 4.8 |  |  | RL Voltage | 460
Service Factor |  |  |  |  | RL Amperage | 4.8
Suction ESP
[5 empty] | Total ESP | 2
Brake Horse Power
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
-

## KEF-2
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: KEF-2 |  |  | Serves: KITCHEN HOOD 2 |  |  |  |  | SUBMITTAL
Unit Data |  |  |  |  | Drive Data
MFG |  | GREENHECK |  |  | Motor Sheave Size
Model Num |  | USF-16 |  |  | Motor Bore Size
Serial Num |  |  |  |  | Fan Sheave Size
Type |  | BELTED VENT FAN |  |  | Fan Bore Size
Belt CL Distance
Motor Data |  |  |  |  | No of Belts
Motor MFG |  |  |  |  | Belt Size
Frame |  | 56
Horsepower |  | 2 |  |  | Test Data
Motor Rpm |  | 1725 |  |  |  | Design | Actual
Phase |  | 3 |  |  | CFM | 2400
Voltage (rated) |  | 460 |  |  | Fan RPM | 1691
Amperage (rated) |  | 3.4 |  |  | RL Voltage | 460
Service Factor |  |  |  |  | RL Amperage | 3.4
Suction ESP
[5 empty] | Total ESP | 2.5
Brake Horse Power
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
-

## KEF-3
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: KEF-3 |  |  | Serves: KITCHEN HOOD 3 |  |  |  |  | SUBMITTAL
Unit Data |  |  |  |  | Drive Data
MFG |  | GREENHECK |  |  | Motor Sheave Size
Model Num |  | USF-16 |  |  | Motor Bore Size
Serial Num |  |  |  |  | Fan Sheave Size
Type |  | BELTED VENT FAN |  |  | Fan Bore Size
Belt CL Distance
Motor Data |  |  |  |  | No of Belts
Motor MFG |  |  |  |  | Belt Size
Frame |  | 56
Horsepower |  | 2 |  |  | Test Data
Motor Rpm |  | 1725 |  |  |  | Design | Actual
Phase |  | 3 |  |  | CFM | 2300
Voltage (rated) |  | 460 |  |  | Fan RPM | 1674
Amperage (rated) |  | 3.4 |  |  | RL Voltage | 460
Service Factor |  |  |  |  | RL Amperage | 3.4
Suction ESP
[5 empty] | Total ESP | 2.5
Brake Horse Power
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
-

## KEF-4
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: KEF-4 |  |  | Serves: KITCHEN HOOD 4 |  |  |  |  | SUBMITTAL
Unit Data |  |  |  |  | Drive Data
MFG |  | GREENHECK |  |  | Motor Sheave Size
Model Num |  | USF-16 |  |  | Motor Bore Size
Serial Num |  |  |  |  | Fan Sheave Size
Type |  | BELTED VENT FAN |  |  | Fan Bore Size
Belt CL Distance
Motor Data |  |  |  |  | No of Belts
Motor MFG |  |  |  |  | Belt Size
Frame |  | 145T
Horsepower |  | 2 |  |  | Test Data
Motor Rpm |  | 1725 |  |  |  | Design | Actual
Phase |  | 3 |  |  | CFM | 2700
Voltage (rated) |  | 460 |  |  | Fan RPM | 1634
Amperage (rated) |  | 3.4 |  |  | RL Voltage | 460
Service Factor |  |  |  |  | RL Amperage | 3.4
Suction ESP
[5 empty] | Total ESP | 2
Brake Horse Power
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
-

## KEF-5
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: KEF-5 |  |  | Serves: KITCHEN HOOD 5 |  |  |  |  | SUBMITTAL
Unit Data |  |  |  |  | Drive Data
MFG |  | GREENHECK |  |  | Motor Sheave Size
Model Num |  | USF-13 |  |  | Motor Bore Size
Serial Num |  |  |  |  | Fan Sheave Size
Type |  | BELTED VENT FAN |  |  | Fan Bore Size
Belt CL Distance
Motor Data |  |  |  |  | No of Belts
Motor MFG |  |  |  |  | Belt Size
Frame |  | 145T
Horsepower |  | 1.5 |  |  | Test Data
Motor Rpm |  | 175 |  |  |  | Design | Actual
Phase |  | 3 |  |  | CFM | 1400
Voltage (rated) |  | 460 |  |  | Fan RPM | 2003
Amperage (rated) |  | 3 |  |  | RL Voltage | 460
Service Factor |  |  |  |  | RL Amperage | 3
Suction ESP
[5 empty] | Total ESP | 2.5
Brake Horse Power
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
-

## DWEF-1
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: DWEF-1 |  |  | Serves: WAREWASH |  |  |  |  | SUBMITTAL
Unit Data |  |  |  |  | Test Data
MFG |  | GREENHECK |  |  |  | Design | Actual
Model Num |  | G-160-VG |  |  | CFM | 2850
Serial Num |  |  |  |  | Fan RPM | 1661
Type |  | CRE |  |  | RL Voltage | 460
[5 empty] | RL Amperage | 3.2
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 2
Frame
Horsepower |  | 2
Motor Rpm |  | 1725
Phase |  | 3
Voltage (rated) |  | 460
Amperage (rated) |  | 3.2
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
-

## EF-CEP-1
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: EF-CEP-1 |  |  | Serves: CHILLER ROOM EX |  |  |  |  | SUBMITTAL
Unit Data |  |  |  |  | Test Data
MFG |  | GREENHECK |  |  |  | Design | Actual
Model Num |  | G-160-VG |  |  | CFM | 2850
Serial Num |  |  |  |  | Fan RPM | 1661
Type |  | CRE |  |  | RL Voltage | 460
[5 empty] | RL Amperage | 3.2
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 2
Frame
Horsepower |  | 2
Motor Rpm |  | 1725
Phase |  | 3
Voltage (rated) |  | 460
Amperage (rated) |  | 3.2
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
-

## EF-G-1
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: EF-G-1 |  |  | Serves: AHU-G-1 GENERAL EX |  |  |  |  | SUBMITTAL
Unit Data |  |  |  |  | Test Data
MFG |  | GREENHECK |  |  |  | Design | Actual
Model Num |  | CUE-300HP-VG |  |  | CFM | 5450
Serial Num |  |  |  |  | Fan RPM | 800
Type |  | CRE |  |  | RL Voltage | 460
[5 empty] | RL Amperage | 9.3
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 1.5
Frame
Horsepower |  | 7.5
Motor Rpm |  | 1200
Phase |  | 3
Voltage (rated) |  | 460
Amperage (rated) |  | 9.3
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
-

## EF-G-1A
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: EF-G-1A |  |  | Serves: MED GAS MANIFOLD |  |  |  |  | SUBMITTAL
Unit Data |  |  |  |  | Test Data
MFG |  | GREENHECK |  |  |  | Design | Actual
Model Num |  | G-098-VG |  |  | CFM | 500
Serial Num |  |  |  |  | Fan RPM | 1703
Type |  | CRE |  |  | RL Voltage | 115
[5 empty] | RL Amperage | 2.85
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 1
Frame
Horsepower |  | 0.25
Motor Rpm |  | 1725
Phase |  | 1
Voltage (rated) |  | 115
Amperage (rated) |  | 2.85
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
-

## EF-G-3
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: EF-G-3 |  |  | Serves: AHU-G-3 GENERAL EX |  |  |  |  | SUBMITTAL
Unit Data |  |  |  |  | Test Data
MFG |  | GREENHECK |  |  |  | Design | Actual
Model Num |  | G-099-VG |  |  | CFM | 700
Serial Num |  |  |  |  | Fan RPM | 1652
Type |  | CRE |  |  | RL Voltage | 115
[5 empty] | RL Amperage | 2.85
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 1
Frame
Horsepower |  | 0.25
Motor Rpm |  | 1725
Phase |  | 1
Voltage (rated) |  | 115
Amperage (rated) |  | 2.85
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
-

## EF-1-2
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: EF-1-2 |  |  | Serves: CENTRAL STERILE EX |  |  |  |  | SUBMITTAL
Unit Data |  |  |  |  | Drive Data
MFG |  | GREENHECK |  |  | Motor Sheave Size
Model Num |  | USF-27 |  |  | Motor Bore Size
Serial Num |  |  |  |  | Fan Sheave Size
Type |  | BELTED VENT FAN |  |  | Fan Bore Size
Belt CL Distance
Motor Data |  |  |  |  | No of Belts
Motor MFG |  |  |  |  | Belt Size
Frame |  | 184T
Horsepower |  | 5 |  |  | Test Data
Motor Rpm |  | 1725 |  |  |  | Design | Actual
Phase |  | 3 |  |  | CFM | 8600
Voltage (rated) |  | 460 |  |  | Fan RPM | 1051
Amperage (rated) |  | 7.6 |  |  | RL Voltage | 460
Service Factor |  |  |  |  | RL Amperage | 7.6
Suction ESP
[5 empty] | Total ESP | 1.5
Brake Horse Power
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
-

## EF-1-2A
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: EF-1-2A |  |  | Serves: CART WASH |  |  |  |  | SUBMITTAL
Unit Data |  |  |  |  | Drive Data
MFG |  | GREENHECK |  |  | Motor Sheave Size
Model Num |  | USF-12 |  |  | Motor Bore Size
Serial Num |  |  |  |  | Fan Sheave Size
Type |  | BELTED VENT FAN |  |  | Fan Bore Size
Belt CL Distance
Motor Data |  |  |  |  | No of Belts
Motor MFG |  |  |  |  | Belt Size
Frame |  | 56
Horsepower |  | 0.5 |  |  | Test Data
Motor Rpm |  | 1725 |  |  |  | Design | Actual
Phase |  | 1 |  |  | CFM | 700
Voltage (rated) |  | 115 |  |  | Fan RPM | 1359
Amperage (rated) |  |  |  |  | RL Voltage | 115
Service Factor |  |  |  |  | RL Amperage
Suction ESP
[5 empty] | Total ESP | 1
Brake Horse Power
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
-

## EF-1-3
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: EF-1-3 |  |  | Serves: AHU-1-3 GENERAL EX |  |  |  |  | SUBMITTAL
Unit Data |  |  |  |  | Test Data
MFG |  | GREENHECK |  |  |  | Design | Actual
Model Num |  | CUE-200-VG |  |  | CFM | 4600
Serial Num |  |  |  |  | Fan RPM | 1241
Type |  | CRE |  |  | RL Voltage | 460
[5 empty] | RL Amperage | 4.3
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 1.5
Frame
Horsepower |  | 3
Motor Rpm |  | 1350
Phase |  | 3
Voltage (rated) |  | 460
Amperage (rated) |  | 4.3
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
-

## EF-1-4
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: EF-1-4 |  |  | Serves: AHU-1-4 GENERAL EX |  |  |  |  | SUBMITTAL
Unit Data |  |  |  |  | Drive Data
MFG |  | GREENHECK |  |  | Motor Sheave Size
Model Num |  | USF-30 |  |  | Motor Bore Size
Serial Num |  |  |  |  | Fan Sheave Size
Type |  | BELTED VENT FAN |  |  | Fan Bore Size
Belt CL Distance
Motor Data |  |  |  |  | No of Belts
Motor MFG |  |  |  |  | Belt Size
Frame |  | 184T
Horsepower |  | 5 |  |  | Test Data
Motor Rpm |  | 1725 |  |  |  | Design | Actual
Phase |  | 3 |  |  | CFM | 9100
Voltage (rated) |  | 460 |  |  | Fan RPM | 794
Amperage (rated) |  | 7.6 |  |  | RL Voltage | 460
Service Factor |  |  |  |  | RL Amperage | 7.6
Suction ESP
[5 empty] | Total ESP | 1.5
Brake Horse Power
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
-

## EF-1-4A
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: EF-1-4A |  |  | Serves: MRI PURGE EX |  |  |  |  | SUBMITTAL
Unit Data |  |  |  |  | Test Data
MFG |  | GREENHECK |  |  |  | Design | Actual
Model Num |  | G-140HP-VG |  |  | CFM | 950
Serial Num |  |  |  |  | Fan RPM | 1648
Type |  | CRE |  |  | RL Voltage | 115
[5 empty] | RL Amperage | 6.4
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 1
Frame
Horsepower |  | 0.5
Motor Rpm |  | 1725
Phase |  | 1
Voltage (rated) |  | 115
Amperage (rated) |  | 6.4
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
-

## EF-2-1A
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: EF-2-1A |  |  | Serves: AHU-2-1 GENERAL EX |  |  |  |  | SUBMITTAL
Unit Data |  |  |  |  | Test Data
MFG |  | GREENHECK |  |  |  | Design | Actual
Model Num |  | G-200HP-VG |  |  | CFM | 3900
Serial Num |  |  |  |  | Fan RPM | 1366
Type |  | CRE |  |  | RL Voltage | 460
[5 empty] | RL Amperage | 4.3
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 1.5
Frame
Horsepower |  | 3
Motor Rpm |  | 1560
Phase |  | 3
Voltage (rated) |  | 460
Amperage (rated) |  | 4.3
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
-

## EF-2-1B
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: EF-2-1B |  |  | Serves: AHU-2-1 GENERAL EX |  |  |  |  | SUBMITTAL
Unit Data |  |  |  |  | Test Data
MFG |  | GREENHECK |  |  |  | Design | Actual
Model Num |  | G-160-VG |  |  | CFM | 2700
Serial Num |  |  |  |  | Fan RPM | 1480
Type |  | CRE |  |  | RL Voltage | 460
[5 empty] | RL Amperage | 3.2
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 1.5
Frame
Horsepower |  | 2
Motor Rpm |  | 1725
Phase |  | 3
Voltage (rated) |  | 460
Amperage (rated) |  | 3.2
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
-

## EF-3-1A
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: EF-3-1A |  |  | Serves: AHU-3-1 GENERAL EX |  |  |  |  | SUBMITTAL
Unit Data |  |  |  |  | Test Data
MFG |  | GREENHECK |  |  |  | Design | Actual
Model Num |  | G-160-VG |  |  | CFM | 2950
Serial Num |  |  |  |  | Fan RPM | 1525
Type |  | CRE |  |  | RL Voltage | 460
[5 empty] | RL Amperage | 3.2
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 1.5
Frame
Horsepower |  | 2
Motor Rpm |  | 1725
Phase |  | 3
Voltage (rated) |  | 460
Amperage (rated) |  | 3.2
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
-

## EF-3-1B
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: EF-3-1B |  |  | Serves: AHU-3-1 GENERAL EX |  |  |  |  | SUBMITTAL
Unit Data |  |  |  |  | Test Data
MFG |  | GREENHECK |  |  |  | Design | Actual
Model Num |  | G-160-VG |  |  | CFM | 2950
Serial Num |  |  |  |  | Fan RPM | 1525
Type |  | CRE |  |  | RL Voltage | 460
[5 empty] | RL Amperage | 3.2
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 1.5
Frame
Horsepower |  | 2
Motor Rpm |  | 1725
Phase |  | 3
Voltage (rated) |  | 460
Amperage (rated) |  | 3.2
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
-

## EF-4-1A
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: EF-4-1A |  |  | Serves: AHU-4-1 GENERAL EX |  |  |  |  | SUBMITTAL
Unit Data |  |  |  |  | Test Data
MFG |  | GREENHECK |  |  |  | Design | Actual
Model Num |  | G-200HP-VG |  |  | CFM | 2550
Serial Num |  |  |  |  | Fan RPM | 1167
Type |  | CRE |  |  | RL Voltage | 460
[5 empty] | RL Amperage | 4.7
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 1.5
Frame
Horsepower |  | 2
Motor Rpm |  | 1350
Phase |  | 3
Voltage (rated) |  | 460
Amperage (rated) |  | 4.7
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
-

## EF-4-1B
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: EF-4-1A |  |  | Serves: AHU-4-1 GENERAL EX |  |  |  |  | SUBMITTAL
Unit Data |  |  |  |  | Test Data
MFG |  | GREENHECK |  |  |  | Design | Actual
Model Num |  | G-160-VG |  |  | CFM | 2600
Serial Num |  |  |  |  | Fan RPM | 1462
Type |  | CRE |  |  | RL Voltage | 460
[5 empty] | RL Amperage | 3.2
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 1.5
Frame
Horsepower |  | 2
Motor Rpm |  | 1725
Phase |  | 3
Voltage (rated) |  | 460
Amperage (rated) |  | 3.2
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
-

## EF-ISO-1AB
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: EF-ISO-1A/B |  |  | Serves: 2ND-4TH FLR ISO EX |  |  |  |  | SUBMITTAL
Unit Data |  |  |  |  | Drive Data
MFG |  | GREENHECK |  |  | Motor Sheave Size
Model Num |  | VEKTOR-H-30 |  |  | Motor Bore Size
Serial Num |  |  |  |  | Fan Sheave Size
Type |  | FUME EXHAUST |  |  | Fan Bore Size
Belt CL Distance
Motor Data |  |  |  |  | No of Belts
Motor MFG |  | BALDOR |  |  | Belt Size
Frame |  | 254T
Horsepower |  | 15 |  |  | Test Data
Motor Rpm |  | 1725 |  |  |  | Design | Actual
Phase |  | 3 |  |  | CFM | 9050
Voltage (rated) |  | 460 |  |  | Fan RPM | 1126
Amperage (rated) |  |  |  |  | RL Voltage | 460
Service Factor |  |  |  |  | RL Amperage
Suction ESP
[5 empty] | Total ESP | 2.537
Brake Horse Power
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
-

## EF-ISO-2AB
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: EF-ISO-2A/B |  |  | Serves: AHU-G-2 LAB & PHARM EX |  |  |  |  | SUBMITTAL
Unit Data |  |  |  |  | Drive Data
MFG |  | GREENHECK |  |  | Motor Sheave Size
Model Num |  | VEKTOR-H-24 |  |  | Motor Bore Size
Serial Num |  |  |  |  | Fan Sheave Size
Type |  | FUME EXHAUST |  |  | Fan Bore Size
Belt CL Distance
Motor Data |  |  |  |  | No of Belts
Motor MFG |  | BALDOR |  |  | Belt Size
Frame |  | 215T
Horsepower |  | 10 |  |  | Test Data
Motor Rpm |  | 1725 |  |  |  | Design | Actual
Phase |  | 3 |  |  | CFM | 7050
Voltage (rated) |  | 460 |  |  | Fan RPM | 1232
Amperage (rated) |  |  |  |  | RL Voltage | 460
Service Factor |  |  |  |  | RL Amperage
Suction ESP
[5 empty] | Total ESP | 2.539
Brake Horse Power
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
-

## EF-ISO-3
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: EF-ISO-3 |  |  | Serves: ED & TRIAGE |  |  |  |  | SUBMITTAL
Unit Data |  |  |  |  | Drive Data
MFG |  | GREENHECK |  |  | Motor Sheave Size
Model Num |  | USF-24 |  |  | Motor Bore Size
Serial Num |  |  |  |  | Fan Sheave Size
Type |  | BELTED VENT FAN |  |  | Fan Bore Size
Belt CL Distance
Motor Data |  |  |  |  | No of Belts
Motor MFG |  |  |  |  | Belt Size
Frame |  | 182T
Horsepower |  | 3 |  |  | Test Data
Motor Rpm |  | 1725 |  |  |  | Design | Actual
Phase |  | 3 |  |  | CFM | 5550
Voltage (rated) |  | 460 |  |  | Fan RPM | 960
Amperage (rated) |  | 4.8 |  |  | RL Voltage | 460
Service Factor |  |  |  |  | RL Amperage | 4.8
Suction ESP
[5 empty] | Total ESP | 1.5
Brake Horse Power
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
-

## EF-ISO-4
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: EF-ISO-4 |  |  | Serves: NUC MED/HOT LAB |  |  |  |  | SUBMITTAL
Unit Data |  |  |  |  | Drive Data
MFG |  | GREENHECK |  |  | Motor Sheave Size
Model Num |  | USF-10 |  |  | Motor Bore Size
Serial Num |  |  |  |  | Fan Sheave Size
Type |  | BELTED VENT FAN |  |  | Fan Bore Size
Belt CL Distance
Motor Data |  |  |  |  | No of Belts
Motor MFG |  |  |  |  | Belt Size
Frame |  | 56
Horsepower |  | 0.75 |  |  | Test Data
Motor Rpm |  | 1725 |  |  |  | Design | Actual
Phase |  | 3 |  |  | CFM | 5550
Voltage (rated) |  | 460 |  |  | Fan RPM | 2218
Amperage (rated) |  | 1.6 |  |  | RL Voltage | 460
Service Factor |  |  |  |  | RL Amperage | 1.6
Suction ESP
[5 empty] | Total ESP | 1.5
Brake Horse Power
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
-

## EF-ISO-5AB
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: EF-ISO-5A/B |  |  | Serves: EXAM 11 (A.I.I) |  |  |  |  | SUBMITTAL
Unit Data |  |  |  |  | Drive Data
MFG |  | GREENHECK |  |  | Motor Sheave Size
Model Num |  | VEKTOR-H-10 |  |  | Motor Bore Size
Serial Num |  |  |  |  | Fan Sheave Size
Type |  | FUME EXHAUST |  |  | Fan Bore Size
Belt CL Distance
Motor Data |  |  |  |  | No of Belts
Motor MFG |  | BALDR |  |  | Belt Size
Frame |  | 56
Horsepower |  | 0.75 |  |  | Test Data
Motor Rpm |  | 1725 |  |  |  | Design | Actual
Phase |  | 3 |  |  | CFM | 450
Voltage (rated) |  | 460 |  |  | Fan RPM | 2661
Amperage (rated) |  |  |  |  | RL Voltage | 460
Service Factor |  |  |  |  | RL Amperage
Suction ESP
[5 empty] | Total ESP | 1.508
Brake Horse Power
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
-

## SF-CEP-1
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: SF-CEP-1 |  |  | Serves: CHILLER RM FCUS |  |  |  |  | SUBMITTAL
Unit Data |  |  |  |  | Test Data
MFG |  | GREENHECK |  |  |  | Design | Actual
Model Num |  | RS2-24-612-VG |  |  | CFM | 2800
Serial Num |  |  |  |  | Fan RPM | 1526
Type |  | ROOF SUPPLY FAN |  |  | RL Voltage | 460
[5 empty] | RL Amperage | 3.2
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 1
Frame
Horsepower |  | 2
Motor Rpm |  | 1725
Phase |  | 3
Voltage (rated) |  | 460
Amperage (rated) |  | 3.2
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
-

## Hood 1
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: HOOD #1 |  | Area: KITCHEN H.0014 |  |  |  | SUBMITTAL
Unit Data |  |  | Test Data Supply
MFG | CAPTIVEAIRE |  | AK factor
Model Num | 6624 ND-2-PSP-F |  | Total AK Area
Job / Serial Num |  |  |  | PRELIM | FINAL
Type | TYPE 1 CANOPY |  | Reading1 FPM
Hood Length | 187 |  | Reading2 FPM
Hood Width | 66 |  | Reading3 FPM
Supply Plenum Type | PSP |  | Reading4 FPM
Supply Plenum Width | 16 |  | Reading5 FPM
Supply Plenum Length | 187 |  | Reading6 FPM
Reading7 FPM
Test Data Exhaust |  |  | Reading8 FPM
Filter Type | CAPTRATE SOLO |  | Reading9 FPM
Filter Size 1 | 20X16 |  | Reading10 FPM
Filter Qty 1 | 11
Filter AK factor size 1 | 2.08
Filter Total AK Area 1 | 22.88
Ave FPM(corr)
| PRELIM | FINAL | CFM | 2287
Filter1 FPM
Filter2 FPM
Filter3 FPM
Filter4 FPM
Filter5 FPM
Filter6 FPM
Filter7 FPM
Filter8 FPM
Filter9 FPM
Filter10 FPM
Filter11 FPM
Filter Ave FPM
CFM | 3584

## Hood 2
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: HOOD #2 |  | Area: KITCHEN H.0014 |  |  |  | SUBMITTAL
Unit Data |  |  | Test Data Supply
MFG | CAPTIVEAIRE |  | AK factor
Model Num | 6624 ND-2-PSP-F |  | Total AK Area
Job / Serial Num |  |  |  | PRELIM | FINAL
Type | TYPE 1 CANOPY |  | Reading1 FPM
Hood Length | 108 |  | Reading2 FPM
Hood Width | 66 |  | Reading3 FPM
Supply Plenum Type | PSP |  | Reading4 FPM
Supply Plenum Width | 16 |  | Reading5 FPM
Supply Plenum Length | 108 |  | Reading6 FPM
Reading7 FPM
Test Data Exhaust |  |  | Reading8 FPM
Filter Type | CAPTRATE SOLO |  | Reading9 FPM
Filter Size 1 | 20X16 |  | Reading10 FPM
Filter Qty 1 | 6
Filter AK factor size 1 | 2.08
Filter Total AK Area 1 | 12.48
Ave FPM(corr)
| PRELIM | FINAL | CFM | 1660
Filter1 FPM
Filter2 FPM
Filter3 FPM
Filter4 FPM
Filter5 FPM
Filter6 FPM
Filter Ave FPM
CFM | 2385

## Hood 3
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: HOOD #3 |  | Area: KITCHEN H.0014 |  |  |  | SUBMITTAL
Unit Data |  |  | Test Data Supply
MFG | CAPTIVEAIRE |  | AK factor
Model Num | 6624 ND-2-PSP-F |  | Total AK Area
Job / Serial Num |  |  |  | PRELIM | FINAL
Type | TYPE 1 CANOPY |  | Reading1 FPM
Hood Length | 103 |  | Reading2 FPM
Hood Width | 66 |  | Reading3 FPM
Supply Plenum Type | PSP |  | Reading4 FPM
Supply Plenum Width | 16 |  | Reading5 FPM
Supply Plenum Length | 115 |  | Reading6 FPM
Reading7 FPM
Test Data Exhaust |  |  | Reading8 FPM
Filter Type | CAPTRATE SOLO |  | Reading9 FPM
Filter Size 1 | 20X16 |  | Reading10 FPM
Filter Qty 1 | 6
Filter AK factor size 1 | 2.08
Filter Total AK Area 1 | 12.48
Ave FPM(corr)
| PRELIM | FINAL | CFM | 1774
Filter1 FPM
Filter2 FPM
Filter3 FPM
Filter4 FPM
Filter5 FPM
Filter6 FPM
Filter Ave FPM
CFM | 2275

## Hood 4
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: HOOD #4 |  | Area: SERVERY H.0008 |  |  |  | SUBMITTAL
Unit Data |  |  | Test Data Supply
MFG | CAPTIVEAIRE |  | AK factor
Model Num | 6024 ND-2-PSP-F |  | Total AK Area
Job / Serial Num |  |  |  | PRELIM | FINAL
Type | TYPE 1 CANOPY |  | Reading1 FPM
Hood Length | 122 |  | Reading2 FPM
Hood Width | 60 |  | Reading3 FPM
Supply Plenum Type | PSP |  | Reading4 FPM
Supply Plenum Width | 16 |  | Reading5 FPM
Supply Plenum Length | 134 |  | Reading6 FPM
Reading7 FPM
Test Data Exhaust |  |  | Reading8 FPM
Filter Type | CAPTRATE SOLO |  | Reading9 FPM
Filter Size 1 | 20X16 |  | Reading10 FPM
Filter Qty 1 | 7
Filter AK factor size 1 | 2.08
Filter Total AK Area 1 | 14.56
Ave FPM(corr)
| PRELIM | FINAL | CFM | 2076
Filter1 FPM
Filter2 FPM
Filter3 FPM
Filter4 FPM
Filter5 FPM
Filter6 FPM
Filter7 FPM
Filter Ave FPM
CFM | 2643

## Hood 5
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: HOOD #5 |  | Area: SERVERY H.0008 |  |  |  | SUBMITTAL
Unit Data |  |  | Test Data Supply
MFG | CAPTIVEAIRE |  | AK factor
Model Num | 6024 ND-2-PSP-F |  | Total AK Area
Job / Serial Num |  |  |  | PRELIM | FINAL
Type | TYPE 1 CANOPY |  | Reading1 FPM
Hood Length | 122 |  | Reading2 FPM
Hood Width | 60 |  | Reading3 FPM
Reading4 FPM
Reading5 FPM
Reading6 FPM
Reading7 FPM
Test Data Exhaust |  |  | Reading8 FPM
Filter Type | CAPTRATE SOLO |  | Reading9 FPM
Filter Size 1 | 16X16 |  | Reading10 FPM
Filter Qty 1 | 4
Filter AK factor size 1 | 1.62
Filter Total AK Area 1 | 6.48
Ave FPM(corr)
| PRELIM | FINAL | CFM
Filter1 FPM
Filter2 FPM
Filter3 FPM
Filter4 FPM
Filter5 FPM
Filter6 FPM
Filter7 FPM
Filter Ave FPM
CFM | 1350

## Boilers
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: BOILERS |  | Service: HEATING & DHW |  |  |  |  | SUBMITTAL
Unit Data | HWB-1 |  | HWB-2 |  | HWB-3
Manufacturer | SUPERIOR |  | SUPERIOR |  | SUPERIOR
Model Number | CH-6000-W160-WP-GP2 |  | CH-6000-W160-WP-GP2 |  | CH-6000-W160-WP-GP2
Serial Number
Test Data | Design | Actual | Design | Actual | Design | Actual
Water Flow GPM | 359 |  | 359 |  | 359
Water Press. Drop | 5.1 |  | 5.1 |  | 5.1

## Cooling Tower
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
DATA FROM SCHEDULE
Asset: CT-1 |  |  | Asset: CT-2 |  |  | NO SUBMITTAL
Unit Data |  |  | Unit Data
Manufacturer | MARLEY |  | Manufacturer | MARLEY
Model Num | NC8405RAN4 |  | Model Num | NC8405RAN4
Serial Num |  |  | Serial Num
Service | CHILLER 1 |  | Service | CHILLER 2
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
CW GPM | 1000 |  | CW GPM | 1000
EWT (F) | 100 |  | EWT (F) | 100
LWT (F) | 85 |  | LWT (F) | 85
Water Pres Delta P |  |  | Water Pres Delta P
Asset: CT-3
Unit Data
Manufacturer | MARLEY
Model Num | NC8405RAN4
Serial Num
Service | CHILLER 3
Test Data
| Design | Actual
CW GPM | 1000
EWT (F) | 100
LWT (F) | 85
Water Pres Delta P

## Chiller WC
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: CH-1 |  |  | Asset: CH-2 |  |  | SUBMITTAL
UNIT DATA |  |  | UNIT DATA
Unit Description |  |  | Unit Description
Manufacturer | YORK |  | Manufacturer | YORK
Model Number | YKCKCPQ7-ESHS |  | Model Number | YKCKCPQ7-ESHS
Serial Number |  |  | Serial Number
EVAPORATOR DATA | Design | Actual | EVAPORATOR DATA | Design | Actual
Flow GPM | 996.5 |  | Flow GPM | 996.5
Pressure Drop | 31.3 |  | Pressure Drop | 31.3
CONDENSER DATA | Design | Actual | CONDENSER DATA | Design | Actual
Flow GPM | 1000 |  | Flow GPM | 1000
Pressure Drop | 11.5 |  | Pressure Drop | 11.5
Asset: CH-3
UNIT DATA
Unit Description
Manufacturer | YORK
Model Number | YKCKCPQ7-ESHS
Serial Number
EVAPORATOR DATA | Design | Actual
Flow GPM | 996.5
Pressure Drop | 31.3
CONDENSER DATA | Design | Actual
Flow GPM | 1000
Pressure Drop | 11.5

## CHP-1
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: CHP-1 |  |  |  |  | SUBMITTAL
Unit Data |  | Test Data
| Actual |  | Design | Actual
MFG | ARMSTRONG | Pump Off Pressure (psi)
Model Num | SERIES 4300-4X4X8 | Pump Dead Head (ft)
Serial Num |  | Act. Impellar Dia (in)
Service | CH-1 (CHW) | Valve Open GPM
Pump RPM |  | Valve Open Diff (ft)
GPM/Head | 1000 / 150 | Discharge Pressure (ft)
Impellar Diameter | 7.02 | Suction Pressure (ft)
Total Head Pressure (ft)
Motor Data |  | Final GPM
| Actual | Motor Frequency (HZ)
Motor MFG | BALDOR | System Set Point
Frame | 326TSC | RL Voltage | 460
Horsepower | 60 | RL Amperage
Motor RPM | 3580 | BHP | 49.73
Phase | 3
Voltage | 460
Amperage
Service Factor
Efficiency
Power Factor

## CHP-2
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: CHP-2 |  |  |  |  | SUBMITTAL
Unit Data |  | Test Data
| Actual |  | Design | Actual
MFG | ARMSTRONG | Pump Off Pressure (psi)
Model Num | SERIES 4300-4X4X8 | Pump Dead Head (ft)
Serial Num |  | Act. Impellar Dia (in)
Service | CH-2 (CHW) | Valve Open GPM
Pump RPM |  | Valve Open Diff (ft)
GPM/Head | 1000 / 150 | Discharge Pressure (ft)
Impellar Diameter | 7.02 | Suction Pressure (ft)
Total Head Pressure (ft)
Motor Data |  | Final GPM
| Actual | Motor Frequency (HZ)
Motor MFG | BALDOR | System Set Point
Frame | 326TSC | RL Voltage | 460
Horsepower | 60 | RL Amperage
Motor RPM | 3580 | BHP | 49.73
Phase | 3
Voltage | 460
Amperage
Service Factor
Efficiency
Power Factor

## CHP-3
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: CHP-3 |  |  |  |  | SUBMITTAL
Unit Data |  | Test Data
| Actual |  | Design | Actual
MFG | ARMSTRONG | Pump Off Pressure (psi)
Model Num | SERIES 4300-4X4X8 | Pump Dead Head (ft)
Serial Num |  | Act. Impellar Dia (in)
Service | CH-3 (CHW) | Valve Open GPM
Pump RPM |  | Valve Open Diff (ft)
GPM/Head | 1000 / 150 | Discharge Pressure (ft)
Impellar Diameter | 7.02 | Suction Pressure (ft)
Total Head Pressure (ft)
Motor Data |  | Final GPM
| Actual | Motor Frequency (HZ)
Motor MFG | BALDOR | System Set Point
Frame | 326TSC | RL Voltage | 460
Horsepower | 60 | RL Amperage
Motor RPM | 3580 | BHP | 49.73
Phase | 3
Voltage | 460
Amperage
Service Factor
Efficiency
Power Factor

## CWP-1
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: CWP-1 |  |  |  |  | SUBMITTAL
Unit Data |  | Test Data
| Actual |  | Design | Actual
MFG | ARMSTRONG | Pump Off Pressure (psi)
Model Num | SERIES 4300-4X4X8 | Pump Dead Head (ft)
Serial Num |  | Act. Impellar Dia (in)
Service | CH-1 (CHW) | Valve Open GPM
Pump RPM |  | Valve Open Diff (ft)
GPM/Head | 1000 / 55 | Discharge Pressure (ft)
Impellar Diameter | 10.19 | Suction Pressure (ft)
Total Head Pressure (ft)
Motor Data |  | Final GPM
| Actual | Motor Frequency (HZ)
Motor MFG | BALDOR | System Set Point
Frame | 284TC | RL Voltage | 460
Horsepower | 25 | RL Amperage
Motor RPM | 1780 | BHP | 23.05
Phase | 3
Voltage | 460
Amperage
Service Factor
Efficiency
Power Factor

## CWP-2
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: CWP-2 |  |  |  |  | SUBMITTAL
Unit Data |  | Test Data
| Actual |  | Design | Actual
MFG | ARMSTRONG | Pump Off Pressure (psi)
Model Num | SERIES 4300-4X4X8 | Pump Dead Head (ft)
Serial Num |  | Act. Impellar Dia (in)
Service | CH-2 (CHW) | Valve Open GPM
Pump RPM |  | Valve Open Diff (ft)
GPM/Head | 1000 / 55 | Discharge Pressure (ft)
Impellar Diameter | 10.19 | Suction Pressure (ft)
Total Head Pressure (ft)
Motor Data |  | Final GPM
| Actual | Motor Frequency (HZ)
Motor MFG | BALDOR | System Set Point
Frame | 284TC | RL Voltage | 460
Horsepower | 25 | RL Amperage
Motor RPM | 1780 | BHP | 23.05
Phase | 3
Voltage | 460
Amperage
Service Factor
Efficiency
Power Factor

## CWP-3
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: CWP-3 |  |  |  |  | SUBMITTAL
Unit Data |  | Test Data
| Actual |  | Design | Actual
MFG | ARMSTRONG | Pump Off Pressure (psi)
Model Num | SERIES 4300-4X4X8 | Pump Dead Head (ft)
Serial Num |  | Act. Impellar Dia (in)
Service | CH-3 (CHW) | Valve Open GPM
Pump RPM |  | Valve Open Diff (ft)
GPM/Head | 1000 / 55 | Discharge Pressure (ft)
Impellar Diameter | 10.19 | Suction Pressure (ft)
Total Head Pressure (ft)
Motor Data |  | Final GPM
| Actual | Motor Frequency (HZ)
Motor MFG | BALDOR | System Set Point
Frame | 284TC | RL Voltage | 460
Horsepower | 25 | RL Amperage
Motor RPM | 1780 | BHP | 23.05
Phase | 3
Voltage | 460
Amperage
Service Factor
Efficiency
Power Factor

## HWP-1
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: HWP-1 |  |  |  |  | SUBMITTAL
Unit Data |  | Test Data
| Actual |  | Design | Actual
MFG | ARMSTRONG | Pump Off Pressure (psi)
Model Num | SERIES 4300-3X3X8 | Pump Dead Head (ft)
Serial Num |  | Act. Impellar Dia (in)
Service | HWB-1 (HW) | Valve Open GPM
Pump RPM |  | Valve Open Diff (ft)
GPM/Head | 400 / 150 | Discharge Pressure (ft)
Impellar Diameter | 6.61 | Suction Pressure (ft)
Total Head Pressure (ft)
Motor Data |  | Final GPM
| Actual | Motor Frequency (HZ)
Motor MFG | BALDOR | System Set Point
Frame | 256TC | RL Voltage | 460
Horsepower | 25 | RL Amperage
Motor RPM | 3580 | BHP | 21.26
Phase | 3
Voltage | 460
Amperage
Service Factor
Efficiency
Power Factor

## HWP-2
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: HWP-2 |  |  |  |  | SUBMITTAL
Unit Data |  | Test Data
| Actual |  | Design | Actual
MFG | ARMSTRONG | Pump Off Pressure (psi)
Model Num | SERIES 4300-3X3X8 | Pump Dead Head (ft)
Serial Num |  | Act. Impellar Dia (in)
Service | HWB-2 (HW) | Valve Open GPM
Pump RPM |  | Valve Open Diff (ft)
GPM/Head | 400 / 150 | Discharge Pressure (ft)
Impellar Diameter | 6.61 | Suction Pressure (ft)
Total Head Pressure (ft)
Motor Data |  | Final GPM
| Actual | Motor Frequency (HZ)
Motor MFG | BALDOR | System Set Point
Frame | 256TC | RL Voltage | 460
Horsepower | 25 | RL Amperage
Motor RPM | 3580 | BHP | 21.26
Phase | 3
Voltage | 460
Amperage
Service Factor
Efficiency
Power Factor

## HWP-3
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: HWP-3 |  |  |  |  | SUBMITTAL
Unit Data |  | Test Data
| Actual |  | Design | Actual
MFG | ARMSTRONG | Pump Off Pressure (psi)
Model Num | SERIES 4300-3X3X8 | Pump Dead Head (ft)
Serial Num |  | Act. Impellar Dia (in)
Service | HWB-3 (HW) | Valve Open GPM
Pump RPM |  | Valve Open Diff (ft)
GPM/Head | 400 / 150 | Discharge Pressure (ft)
Impellar Diameter | 6.61 | Suction Pressure (ft)
Total Head Pressure (ft)
Motor Data |  | Final GPM
| Actual | Motor Frequency (HZ)
Motor MFG | BALDOR | System Set Point
Frame | 256TC | RL Voltage | 460
Horsepower | 25 | RL Amperage
Motor RPM | 3580 | BHP | 21.26
Phase | 3
Voltage | 460
Amperage
Service Factor
Efficiency
Power Factor

## PHP-CEP-1
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: PHP-CEP-1 |  |  |  |  | SUBMITTAL
Unit Data |  | Test Data
| Actual |  | Design | Actual
MFG | BELL & GOSSETT | Pump Off Pressure (psi)
Model Num | e9055S-ECM | Pump Dead Head (ft)
Serial Num |  | Act. Impellar Dia (in)
Service | FCU-CEP-1A (HW) | Valve Open GPM
Pump RPM |  | Valve Open Diff (ft)
GPM/Head | 20 / 5 | Discharge Pressure (ft)
Impellar Diameter | 5 | Suction Pressure (ft)
|  | Total Head Pressure (ft) | 5
Motor Data |  | Final GPM | 20
| Actual | Motor Frequency (HZ)
Motor MFG |  | System Set Point
Frame |  | RL Voltage | 230
Horsepower | 1 | RL Amperage
Motor RPM | 1765 | BHP
Phase | 1
Voltage | 230
Amperage
Service Factor
Efficiency
Power Factor

## PHP-CEP-2
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: PHP-CEP-2 |  |  |  |  | SUBMITTAL
Unit Data |  | Test Data
| Actual |  | Design | Actual
MFG | BELL & GOSSETT | Pump Off Pressure (psi)
Model Num | e9055S-ECM | Pump Dead Head (ft)
Serial Num |  | Act. Impellar Dia (in)
Service | FCU-CEP-1B (HW) | Valve Open GPM
Pump RPM |  | Valve Open Diff (ft)
GPM/Head | 20 / 5 | Discharge Pressure (ft)
Impellar Diameter | 5 | Suction Pressure (ft)
|  | Total Head Pressure (ft) | 5
Motor Data |  | Final GPM | 20
| Actual | Motor Frequency (HZ)
Motor MFG |  | System Set Point
Frame |  | RL Voltage | 230
Horsepower | 1 | RL Amperage
Motor RPM | 1765 | BHP
Phase | 1
Voltage | 230
Amperage
Service Factor
Efficiency
Power Factor

## PHP-CEP-3
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: PHP-CEP-3 |  |  |  |  | SUBMITTAL
Unit Data |  | Test Data
| Actual |  | Design | Actual
MFG | BELL & GOSSETT | Pump Off Pressure (psi)
Model Num | e9055S-ECM | Pump Dead Head (ft)
Serial Num |  | Act. Impellar Dia (in)
Service | FCU-CEP-5 (HW) | Valve Open GPM
Pump RPM |  | Valve Open Diff (ft)
GPM/Head | 8 / 5 | Discharge Pressure (ft)
Impellar Diameter | 5 | Suction Pressure (ft)
|  | Total Head Pressure (ft) | 5
Motor Data |  | Final GPM | 8
| Actual | Motor Frequency (HZ)
Motor MFG |  | System Set Point
Frame |  | RL Voltage | 230
Horsepower | 1 | RL Amperage
Motor RPM | 1765 | BHP
Phase | 1
Voltage | 230
Amperage
Service Factor
Efficiency
Power Factor

## PHP-G-1
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: PHP-G-1 |  |  |  |  | SUBMITTAL
Unit Data |  | Test Data
| Actual |  | Design | Actual
MFG | ARMSTRONG | Pump Off Pressure (psi)
Model Num | SERIES 4380-3X3X6 | Pump Dead Head (ft)
Serial Num |  | Act. Impellar Dia (in)
Service | AHU-G-1 | Valve Open GPM
Pump RPM |  | Valve Open Diff (ft)
GPM/Head | 157 / 30 | Discharge Pressure (ft)
Impellar Diameter | 6.16 | Suction Pressure (ft)
Total Head Pressure (ft)
Motor Data |  | Final GPM
| Actual | Motor Frequency (HZ)
Motor MFG | BALDOR | System Set Point
Frame | 182JM | RL Voltage | 460
Horsepower | 3 | RL Amperage
Motor RPM | 1760 | BHP | 1.57
Phase | 3
Voltage | 460
Amperage
Service Factor
Efficiency
Power Factor

## PHP-G-2
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: PHP-G-2 |  |  |  |  | SUBMITTAL
Unit Data |  | Test Data
| Actual |  | Design | Actual
MFG | ARMSTRONG | Pump Off Pressure (psi)
Model Num | SERIES 4380-3X3X6 | Pump Dead Head (ft)
Serial Num |  | Act. Impellar Dia (in)
Service | AHU-G-2 | Valve Open GPM
Pump RPM |  | Valve Open Diff (ft)
GPM/Head | 131 / 30 | Discharge Pressure (ft)
Impellar Diameter | 5.99 | Suction Pressure (ft)
Total Head Pressure (ft)
Motor Data |  | Final GPM
| Actual | Motor Frequency (HZ)
Motor MFG | BALDOR | System Set Point
Frame | 145JM | RL Voltage | 460
Horsepower | 2 | RL Amperage
Motor RPM | 1760 | BHP | 1.37
Phase | 3
Voltage | 460
Amperage
Service Factor
Efficiency
Power Factor

## PHP-G-3
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: PHP-G-3 |  |  |  |  | SUBMITTAL
Unit Data |  | Test Data
| Actual |  | Design | Actual
MFG | ARMSTRONG | Pump Off Pressure (psi)
Model Num | SERIES 4380-4X4X6 | Pump Dead Head (ft)
Serial Num |  | Act. Impellar Dia (in)
Service | AHU-G-3 | Valve Open GPM
Pump RPM |  | Valve Open Diff (ft)
GPM/Head | 304 / 30 | Discharge Pressure (ft)
Impellar Diameter | 6.19 | Suction Pressure (ft)
Total Head Pressure (ft)
Motor Data |  | Final GPM
| Actual | Motor Frequency (HZ)
Motor MFG | BALDOR | System Set Point
Frame | 184JM | RL Voltage | 460
Horsepower | 5 | RL Amperage
Motor RPM | 1765 | BHP | 2.98
Phase | 3
Voltage | 460
Amperage
Service Factor
Efficiency
Power Factor

## PHP-1-2
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: PHP-1-2 |  |  |  |  | SUBMITTAL
Unit Data |  | Test Data
| Actual |  | Design | Actual
MFG | ARMSTRONG | Pump Off Pressure (psi)
Model Num | SERIES 4360-3D | Pump Dead Head (ft)
Serial Num |  | Act. Impellar Dia (in)
Service | AHU-1-2 | Valve Open GPM
Pump RPM |  | Valve Open Diff (ft)
GPM/Head | 200 / 30 | Discharge Pressure (ft)
Impellar Diameter | 6.84 | Suction Pressure (ft)
Total Head Pressure (ft)
Motor Data |  | Final GPM
| Actual | Motor Frequency (HZ)
Motor MFG | BALDOR | System Set Point
Frame | 182JM | RL Voltage | 460
Horsepower | 3 | RL Amperage
Motor RPM | 1760 | BHP | 2.35
Phase | 3
Voltage | 460
Amperage
Service Factor
Efficiency
Power Factor

## PHP-1-3
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: PHP-1-3 |  |  |  |  | SUBMITTAL
Unit Data |  | Test Data
| Actual |  | Design | Actual
MFG | ARMSTRONG | Pump Off Pressure (psi)
Model Num | SERIES 4360-3D | Pump Dead Head (ft)
Serial Num |  | Act. Impellar Dia (in)
Service | AHU-1-3 | Valve Open GPM
Pump RPM |  | Valve Open Diff (ft)
GPM/Head | 204 / 30 | Discharge Pressure (ft)
Impellar Diameter | 6.89 | Suction Pressure (ft)
Total Head Pressure (ft)
Motor Data |  | Final GPM
| Actual | Motor Frequency (HZ)
Motor MFG | BALDOR | System Set Point
Frame | 182JM | RL Voltage | 460
Horsepower | 3 | RL Amperage
Motor RPM | 1760 | BHP | 2.4
Phase | 3
Voltage | 460
Amperage
Service Factor
Efficiency
Power Factor

## PHP-1-4
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: PHP-1-4 |  |  |  |  | SUBMITTAL
Unit Data |  | Test Data
| Actual |  | Design | Actual
MFG | ARMSTRONG | Pump Off Pressure (psi)
Model Num | SERIES 4380-5X5X8 | Pump Dead Head (ft)
Serial Num |  | Act. Impellar Dia (in)
Service | AHU-1-4 | Valve Open GPM
Pump RPM |  | Valve Open Diff (ft)
GPM/Head | 388 / 30 | Discharge Pressure (ft)
Impellar Diameter | 6.96 | Suction Pressure (ft)
Total Head Pressure (ft)
Motor Data |  | Final GPM
| Actual | Motor Frequency (HZ)
Motor MFG | BALDOR | System Set Point
Frame | 184JM | RL Voltage | 460
Horsepower | 5 | RL Amperage
Motor RPM | 1765 | BHP | 3.99
Phase | 3
Voltage | 460
Amperage
Service Factor
Efficiency
Power Factor

## PHP-3-1
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: PHP-3-1 |  |  |  |  | SUBMITTAL
Unit Data |  | Test Data
| Actual |  | Design | Actual
MFG | ARMSTRONG | Pump Off Pressure (psi)
Model Num | SERIES 4380-4X4X8 | Pump Dead Head (ft)
Serial Num |  | Act. Impellar Dia (in)
Service | AHU-3-1 | Valve Open GPM
Pump RPM |  | Valve Open Diff (ft)
GPM/Head | 223 / 30 | Discharge Pressure (ft)
Impellar Diameter | 8.19 | Suction Pressure (ft)
Total Head Pressure (ft)
Motor Data |  | Final GPM
| Actual | Motor Frequency (HZ)
Motor MFG | BALDOR | System Set Point
Frame | 215JP | RL Voltage | 460
Horsepower | 5 | RL Amperage
Motor RPM | 1170 | BHP | 2.42
Phase | 3
Voltage | 460
Amperage
Service Factor
Efficiency
Power Factor

## PHP-4-1
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: PHP-4-1 |  |  |  |  | SUBMITTAL
Unit Data |  | Test Data
| Actual |  | Design | Actual
MFG | ARMSTRONG | Pump Off Pressure (psi)
Model Num | SERIES 4380-4X4X8 | Pump Dead Head (ft)
Serial Num |  | Act. Impellar Dia (in)
Service | AHU-4-1 | Valve Open GPM
Pump RPM |  | Valve Open Diff (ft)
GPM/Head | 226 / 30 | Discharge Pressure (ft)
Impellar Diameter | 8.19 | Suction Pressure (ft)
Total Head Pressure (ft)
Motor Data |  | Final GPM
| Actual | Motor Frequency (HZ)
Motor MFG | BALDOR | System Set Point
Frame | 215JP | RL Voltage | 460
Horsepower | 5 | RL Amperage
Motor RPM | 1170 | BHP | 2.44
Phase | 3
Voltage | 460
Amperage
Service Factor
Efficiency
Power Factor

## PHP-1
National TAB
Project: Westover Hills Baptist Hospital
Address: San Antonio, TX
Asset: PHP-1 |  |  |  |  | SUBMITTAL
Unit Data |  | Test Data
| Actual |  | Design | Actual
MFG | ARMSTRONG | Pump Off Pressure (psi)
Model Num | SERIES 4360-3D | Pump Dead Head (ft)
Serial Num |  | Act. Impellar Dia (in)
Service | DOAS-1 | Valve Open GPM
Pump RPM |  | Valve Open Diff (ft)
GPM/Head | 202 / 30 | Discharge Pressure (ft)
Impellar Diameter | 6.86 | Suction Pressure (ft)
Total Head Pressure (ft)
Motor Data |  | Final GPM
| Actual | Motor Frequency (HZ)
Motor MFG | BALDOR | System Set Point
Frame | 182JM | RL Voltage | 460
Horsepower | 3 | RL Amperage
Motor RPM | 1760 | BHP | 2.38
Phase | 3
Voltage | 460
Amperage
Service Factor
Efficiency
Power Factor

## HW Circuit Setter
National TAB
Project:
Address:
Asset: HW CIRCUIT SETTERS |  |  |  | Service: HOT WATER
Asset | Location | MFG | Model | Size | Type | Design GPM | Setting | Delta P | Final GPM | % to Design

## CHW Circuit Setter
National TAB
Project:
Address:
Asset: CHW CIRCUIT SETTERS |  |  |  | Service: CHILLED WATER
Asset | Location | MFG | Model | Size | Type | Design GPM | Setting | Delta P | Final GPM | % to Design