## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 3400 | 3419 | 2900 | 2871 | 500 | 548 | 14.71% | 16.03%
RTU-2 | DINING | 4000 | 4123 | 3000 | 3100 | 1000 | 1023 | 25% | 24.81%
MUA-1 | KITCHEN HOOD | [8 empty] | 1950 | 2003
EF-1 | KITCHEN HOOD | [10 empty] | 3200 | 3223
EF-2 | RESTROOM | [12 empty] | 150 | 142
TOTALS |  | 7400 | 7542 | 5900 | 5971 | 1500 | 1571 |  |  | 1950 | 2003 | 3200 | 3223 | 150 | 142
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3450 | 3574 |  | FRONT |  | 0.002 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3350 | 3365 |  | SIDE |  | 0.006 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 100 | 209 |  | REAR |  | 0.008 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0053333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | CAPTIVE-AIRE |  | SOLO 10 16X16 |  |  |  | ACPSP |  | 183X12 |  | 1950 |  | 3200 |  | -1250