## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 8750 | 8078 | 7050 | 6421 | 1700 | 1657 | 19.43% | 20.51%
AC-2 | DINING A | 3150 | 3114 | 2400 | 2391 | 750 | 723 | 23.81% | 23.22%
AC-3 | DINING B | 4000 | 3990 | 3000 | 3067 | 1000 | 923 | 25% | 23.13%
AC-4 | DINING B | 2750 | 2979 | 2150 | 2327 | 600 | 652 | 21.82% | 21.89%
AC-5 | DINING B | 2000 | 1943 | 1700 | 1650 | 300 | 293 | 15% | 15.08%
AC-6 | MULTI-PURPOSE | 1100 | 1119 | 920 | 924 | 180 | 195 | 16.36% | 17.43%
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1912 | 1746
EF-2 | HOOD 2 | [10 empty] | 701 | 679
EF-3 | RESTROOM | [12 empty] | 500 | 542
EF-4 | HOOD 3 | [10 empty] | 701 | 641
TOTALS |  | 21750 | 21223 | 17220 | 16780 | 4530 | 4443 |  |  | 0 | 0 | 3314 | 3066 | 500 | 542
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4530 | 4443 |  | FRONT |  | 0.008 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3814 | 3608 |  | SIDE |  | 0.005 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 716 | 835 |  | REAR |  | 0.007 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0066667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390