## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 |  | 2000 | 1968 | 1723 | 1693 | 277 | 275 | 13.85% | 13.97%
RTU-2 |  | 3000 | 3087 | 2722 | 2814 | 278 | 273 | 9.267% | 8.844%
MUA-1 | [9 empty] | 2000 | 2129
EF-1 | [11 empty] | 2475 | 2429
EF-2 | [13 empty] | 80 | 75
TOTALS |  | 5000 | 5055 | 4445 | 4507 | 555 | 548 |  |  | 2000 | 2129 | 2475 | 2429 | 80 | 75
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2555 | 2677 |  | FRONT |  | -0.0141 | [8 empty] | FALSE | TRUE | FALSE
TOTAL EXHAUST |  | 2555 | 2504 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 0
NET AIRFLOW |  | 0 | 173 |  | REAR |  | -0.0175 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.0158 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0